## Sheet1
Water flow friction calculations - small vs. big pipes | [6 empty] | 2016-05-19 19:57 | J. Chaurette
[8 empty] | viscosity (cSt) | 1 | abs. rough. (ft) | 0.00015
Using the Darcy-Weisbach formula for the friction factor | [7 empty] | SG | 1 | length (ft) | 100
Using the Moody diagram for the friction parameter f
Inside dia.
Item | Dia (in) | Rel. rough. | velocity (ft/s) | flow (gpm) | Reynolds no | Laminar/turb. | frict. param. f | frict. fact. (ft/100 ft pipe) | frict comp. | friction (ft) | friction power (hp)
1 | 0.5 | 0.0036 | 8 | 4.896 | 30983.2 | Turbulent | 0.031 | 74.0068 | 51.3103 | 74.0068 | 0.091499
2 | 0.75 | 0.0024 | 8 | 11.0159 | 46474.8 | Turbulent | 0.0277 | 44.0858 | 30.5655 | 44.0858 | 0.12264
3 | 1 | 0.0018 | 8 | 19.5838 | 61966.4 | Turbulent | 0.0258 | 30.7964 | 21.3517 | 30.7964 | 0.1523
4 | 1.5 | 0.0012 | 8 | 44.0636 | 92949.6 | Turbulent | 0.023 | 18.3028 | 12.6897 | 18.3028 | 0.20366
5 | 2 | 0.0009 | 8 | 78.3354 | 123932.8 | Turbulent | 0.0215 | 12.8318 | 8.8966 | 12.8318 | 0.25383
6 | 3 | 0.0006 | 8 | 176.2546 | 185899.2 | Turbulent | 0.0189 | 7.52 | 5.2138 | 7.52 | 0.33471
7 | 4 | 0.00045 | 8 | 313.3415 | 247865.6 | Turbulent | 0.0185 | 5.5207 | 3.8276 | 5.5207 | 0.43683
8 | 6 | 0.0003 | 8 | 705.0184 | 371798.4 | Turbulent | 0.0167 | 3.3224 | 2.3034 | 3.3224 | 0.59149
9 | 8 | 0.000225 | 8 | 1253.366 | 495731.2 | Turbulent | 0.0155 | 2.3127 | 1.6034 | 2.3127 | 0.73199
10 | 10 | 0.00018 | 8 | 1958.3843 | 619664 | Turbulent | 0.0149 | 1.7786 | 1.2331 | 1.7786 | 0.87957
11 | 12 | 0.00015 | 8 | 2820.0734 | 743596.8 | Turbulent | 0.0145 | 1.4423 | 1 | 1.4423 | 1.0271
1 | 0.5 | 0.0036 | 9 | 5.508 | 34856.1 | Turbulent | 0.0305 | 92.1542 | 51.5493 | 92.1542 | 0.12818
2 | 0.75 | 0.0024 | 9 | 12.3929 | 52284.15 | Turbulent | 0.0278 | 55.9975 | 31.3239 | 55.9975 | 0.17525
3 | 1 | 0.0018 | 9 | 22.0318 | 69712.2 | Turbulent | 0.027 | 40.7896 | 22.8169 | 40.7896 | 0.22694
4 | 1.5 | 0.0012 | 9 | 49.5716 | 104568.3 | Turbulent | 0.0245 | 24.6752 | 13.8028 | 24.6752 | 0.30889
5 | 2 | 0.0009 | 9 | 88.1273 | 139424.4 | Turbulent | 0.0225 | 16.9956 | 9.507 | 16.9956 | 0.37823
6 | 3 | 0.0006 | 9 | 198.2864 | 209136.6 | Turbulent | 0.0195 | 9.8197 | 5.493 | 9.8197 | 0.4917
7 | 4 | 0.00045 | 9 | 352.5092 | 278848.8 | Turbulent | 0.018 | 6.7983 | 3.8028 | 6.7983 | 0.60516
8 | 6 | 0.0003 | 9 | 793.1457 | 418273.2 | Turbulent | 0.0165 | 4.1545 | 2.3239 | 4.1545 | 0.8321
9 | 8 | 0.000225 | 9 | 1410.0367 | 557697.6 | Turbulent | 0.0157 | 2.9648 | 1.6585 | 2.9648 | 1.0557
10 | 10 | 0.00018 | 9 | 2203.1824 | 697122 | Turbulent | 0.0155 | 2.3416 | 1.3099 | 2.3416 | 1.3028
11 | 12 | 0.00015 | 9 | 3172.5826 | 836546.4 | Turbulent | 0.0142 | 1.7877 | 1 | 1.7877 | 1.4322
1 | 0.5 | 0.0036 | 10 | 6.12 | 38729 | Turbulent | 0.0301 | 112.2785 | 49.8207 | 112.2785 | 0.17352
2 | 0.75 | 0.0024 | 10 | 13.7699 | 58093.5 | Turbulent | 0.0275 | 68.3867 | 30.3448 | 68.3867 | 0.2378
3 | 1 | 0.0018 | 10 | 24.4798 | 77458 | Turbulent | 0.026 | 48.4924 | 21.5172 | 48.4924 | 0.29977
4 | 1.5 | 0.0012 | 10 | 55.0796 | 116187 | Turbulent | 0.0235 | 29.2198 | 12.9655 | 29.2198 | 0.40642
5 | 2 | 0.0009 | 10 | 97.9192 | 154916 | Turbulent | 0.021 | 19.5835 | 8.6897 | 19.5835 | 0.48424
6 | 3 | 0.0006 | 10 | 220.3182 | 232374 | Turbulent | 0.0195 | 12.1231 | 5.3793 | 12.1231 | 0.67448
7 | 4 | 0.00045 | 10 | 391.6769 | 309832 | Turbulent | 0.0183 | 8.5328 | 3.7862 | 8.5328 | 0.84396
8 | 6 | 0.0003 | 10 | 881.2729 | 464748 | Turbulent | 0.0165 | 5.129 | 2.2759 | 5.129 | 1.1414
9 | 8 | 0.000225 | 10 | 1566.7075 | 619664 | Turbulent | 0.0154 | 3.5903 | 1.5931 | 3.5903 | 1.4204
10 | 10 | 0.00018 | 10 | 2447.9804 | 774580 | Turbulent | 0.015 | 2.7976 | 1.2414 | 2.7976 | 1.7294
11 | 12 | 0.00015 | 10 | 3525.0918 | 929496 | Turbulent | 0.0145 | 2.2537 | 1 | 2.2537 | 2.0061
1 | 0.5 | 0.0036 | 11 | 6.7319 | 42601.9 | Turbulent | 0.0312 | 140.8219 | 50.5946 | 140.8219 | 0.2394
2 | 0.75 | 0.0024 | 11 | 15.1469 | 63902.85 | Turbulent | 0.0285 | 85.7569 | 30.8108 | 85.7569 | 0.32802
3 | 1 | 0.0018 | 11 | 26.9278 | 85203.8 | Turbulent | 0.027 | 60.9325 | 21.8919 | 60.9325 | 0.41434
4 | 1.5 | 0.0012 | 11 | 60.5875 | 127805.7 | Turbulent | 0.0245 | 36.8604 | 13.2432 | 36.8604 | 0.56396
5 | 2 | 0.0009 | 11 | 107.7111 | 170407.6 | Turbulent | 0.0217 | 24.4859 | 8.7973 | 24.4859 | 0.66601
6 | 3 | 0.0006 | 11 | 242.3501 | 255611.4 | Turbulent | 0.019 | 14.2928 | 5.1351 | 14.2928 | 0.87471
7 | 4 | 0.00045 | 11 | 430.8446 | 340815.2 | Turbulent | 0.0182 | 10.2683 | 3.6892 | 10.2683 | 1.1172
8 | 6 | 0.0003 | 11 | 969.4002 | 511222.8 | Turbulent | 0.0168 | 6.3189 | 2.2703 | 6.3189 | 1.5469
9 | 8 | 0.000225 | 11 | 1723.3782 | 681630.4 | Turbulent | 0.0156 | 4.4007 | 1.5811 | 4.4007 | 1.9152
10 | 10 | 0.00018 | 11 | 2692.7785 | 852038 | Turbulent | 0.01495 | 3.3739 | 1.2122 | 3.3739 | 2.2942
11 | 12 | 0.00015 | 11 | 3877.601 | 1022445.6 | Turbulent | 0.0148 | 2.7833 | 1 | 2.7833 | 2.7254
1 | 0.5 | 0.0036 | 12 | 7.3439 | 46474.8 | Turbulent | 0.03 | 161.1439 | 51.4286 | 161.1439 | 0.29885
2 | 0.75 | 0.0024 | 12 | 16.5239 | 69712.2 | Turbulent | 0.027 | 96.6864 | 30.8571 | 96.6864 | 0.40344
3 | 1 | 0.0018 | 12 | 29.3758 | 92949.6 | Turbulent | 0.025 | 67.1433 | 21.4286 | 67.1433 | 0.49808
4 | 1.5 | 0.0012 | 12 | 66.0955 | 139424.4 | Turbulent | 0.023 | 41.1812 | 13.1429 | 41.1812 | 0.68735
5 | 2 | 0.0009 | 12 | 117.5031 | 185899.2 | Turbulent | 0.022 | 29.5431 | 9.4286 | 29.5431 | 0.87662
6 | 3 | 0.0006 | 12 | 264.3819 | 278848.8 | Turbulent | 0.019 | 17.0096 | 5.4286 | 17.0096 | 1.1356
7 | 4 | 0.00045 | 12 | 470.0122 | 371798.4 | Turbulent | 0.0175 | 11.7501 | 3.75 | 11.7501 | 1.3946
8 | 6 | 0.0003 | 12 | 1057.5275 | 557697.6 | Turbulent | 0.0162 | 7.2515 | 2.3143 | 7.2515 | 1.9365
9 | 8 | 0.000225 | 12 | 1880.049 | 743596.8 | Turbulent | 0.0151 | 5.0693 | 1.6179 | 5.0693 | 2.4067
10 | 10 | 0.00018 | 12 | 2937.5765 | 929496 | Turbulent | 0.01475 | 3.9615 | 1.2643 | 3.9615 | 2.9387
11 | 12 | 0.00015 | 12 | 4230.1102 | 1115395.2 | Turbulent | 0.014 | 3.1334 | 1 | 3.1334 | 3.3471
1 | 0.5 | 0.0036 | 13 | 7.9559 | 50347.7 | Turbulent | 0.028 | 176.5123 | 48.6957 | 176.5123 | 0.35463
2 | 0.75 | 0.0024 | 13 | 17.9009 | 75521.55 | Turbulent | 0.0256 | 107.5884 | 29.6812 | 107.5884 | 0.48634
3 | 1 | 0.0018 | 13 | 31.8237 | 100695.4 | Turbulent | 0.025 | 78.8001 | 21.7391 | 78.8001 | 0.63326
4 | 1.5 | 0.0012 | 13 | 71.6034 | 151043.1 | Turbulent | 0.0218 | 45.8091 | 12.6377 | 45.8091 | 0.82831
5 | 2 | 0.0009 | 13 | 127.295 | 201390.8 | Turbulent | 0.021 | 33.0961 | 9.1304 | 33.0961 | 1.0639
6 | 3 | 0.0006 | 13 | 286.4137 | 302086.2 | Turbulent | 0.0189 | 19.8576 | 5.4783 | 19.8576 | 1.4362
7 | 4 | 0.00045 | 13 | 509.1799 | 402781.6 | Turbulent | 0.0174 | 13.7112 | 3.7826 | 13.7112 | 1.763
8 | 6 | 0.0003 | 13 | 1145.6548 | 604172.4 | Turbulent | 0.016 | 8.4053 | 2.3188 | 8.4053 | 2.4317
9 | 8 | 0.000225 | 13 | 2036.7197 | 805563.2 | Turbulent | 0.0159 | 6.2646 | 1.7283 | 6.2646 | 3.222
10 | 10 | 0.00018 | 13 | 3182.3745 | 1006954 | Turbulent | 0.0145 | 4.5704 | 1.2609 | 4.5704 | 3.6729
11 | 12 | 0.00015 | 13 | 4582.6193 | 1208344.8 | Turbulent | 0.0138 | 3.6248 | 1 | 3.6248 | 4.1947
frict. factor compared to
12 " dia. pipe
Absolute roughness 0.00015 ft, viscosity 1 cSt, water