TUTORIAL

CENTRIFUGAL PUMP SYSTEMS

by Jacques Chaurette p. eng.

Fluide Design Inc.

( copyright 2005

Table of contents

1. Different types of pump systems

2. Pressure, friction and flow

3. What is friction in a pump system

4. Flow rate depends on elevation

5. Flow rate depends on friction

6. How does a centrifugal pump produce pressure

7. What can affect the discharge pressure of the pump?

8. Is more pressure better?

9. How to select a centrifugal pump

10. What is total head?

11. What is friction head?

12. The performance or characteristic curve of the pump

13. Examples of total head calculations

14. Calculate the pump discharge pressure from the pump total head

Appendix A

Flow rate and friction loss for different pipe sizes based at different velocities

Appendix B

Formulas and an example of how to do pipe friction calculations

Appendix C

Formulas and an example of how to do pipe fittings friction calculations

Appendix D

Formula and an example of how to do velocity calculation for fluid flow in a pipe

Appendix E

The relationship between pressure and pressure head

Foreword

This tutorial is intended for everyone that has an interest in centrifugal pumps. There is no math, just good, clear explanation of how it works and understanding the principles than calculations details. For those who want to do calculations, some samples have been included in the appendices.

1. Different types of pump systems

There are many types of centrifugal pump systems. Figure 1 shows a typical industrial pump system. There are many variations on this including all kinds of equipment that can be hooked up to these systems that are not shown.

Figure 1 typical industrial pump system.

The system in Figure 2 is a typical domestic water supply system that takes it's water from a shallow well (25 feet down max.) using an end suction centrifugal pump. A jet pump works well in this application (see http://www.watertanks.com/category/43/) .

Figure 2 Typical residential pump system.

The system in Figure 3 is another typical domestic water supply system that takes it's water from a deep well (200-300 feet) and uses a multi-stage submersible pump often called a turbine pump (http://www.webtrol.com/domestic_pumps/8in_turbine.htm).

Figure 3 Typical residential deep well pump system.

2. Pressure, friction and flow

Figure 4 Three important factors for pump systems.

Pressure, friction and flow are three important parameters of a pump system. Pressure is the driving force responsible for the movement of the fluid. Friction is the force that wants to slow down moving fluid particles. Flow is the amount of volume that is displaced per unit time. The unit of flow in North America, at least in the pump industry, is the US gallon per minute, USgpm. From now on I will just use gallons per minute or gpm. In the metric system, flow is in liters per second (L/s) or meters cube per hour (m3/h).

Pressure is in pounds per square inch (psi) or kiloPascals (kPa) in the metric system. In the Imperial system of measurement, the unit psig or pounds per square inch gauge is used, it means that the pressure measurement is relative to the local atmospheric pressure, so that 5 psig is 5 psi above the local atmospheric pressure. The kPa unit scale is intended to be a scale of absolute pressure measurement and there is no kPag, but many people use the kPa as a relative measurement to the local atmosphere and don't bother to specify this. This is not a fault of the metric system but the way people use it.

As an example of the use of pressure and flow units, the pressure available to domestic water systems varies greatly depending on your location with respect to the water treatment plant. It can vary between 30 and 70 psi or more. The following table gives the expected flow rate that you would obtain for different pipe sizes assuming the pipe is kept at the same level as the connection to the main water pressure supply and based on 100 feet of pipe.

Table 1 Expected flow rates for 100 feet of pipe of various diameers based on available pressure.

The unit of friction is....Sorry, I think I need to wait 'til we get closer to the end to explain the reasoning behind this unit.

Figure 5 A typical pump system.

The pump provides the energy necessary to drive the fluid through the system and overcome friction and any elevation difference.

Pressure is increased when fluid particles are forced closer together. For example, in a fire extinguisher work or energy has been spent to pressurize the liquid chemical within, that energy can be stored and used later.

Is it possible to pressurize a liquid within a container that is open? Yes. A good example is a syringe, as you push down on the plunger the pressure increases, and the harder you have to push. There is enough friction as the fluid moves through the needle to produce a great deal of pressure in the body of the syringe.

Figure 6 Pressure produce by fluid friction a syringe.

If we apply this idea to the pump system of Figure 5, even though the discharge pipe end is open, it is possible to have pressure at the pump discharge because there is sufficient friction in the system and elevation difference.

3. What is friction in a pump system

Friction is always present, even in fluids, it is the force that resists the movement of objects.

Figure 7 Friction, the force that resist movement.

When you move a solid on a hard surface, there is friction between the object and the surface. If you put wheels on it, there will be less friction. In the case of moving fluids such as water, there is even less friction but it can become significant for long pipes. Friction can be also be high for short pipes which have a high flow rate and small diameter as in the syringe example.

In fluids, friction occurs between fluid layers that are traveling at different velocities within the pipe (see Figure 8). There is a natural tendency for the fluid velocity to be higher in the center of the pipe than near the wall of the pipe. Friction will also be high for viscous fluids and fluids with suspended particles.

Figure 8 Friction between layers of fluid and the pipe wall.

Another cause of friction is the interaction of the fluid with the pipe wall, the rougher the pipe, the higher the friction.

Friction depends on:

- average velocity of the fluid within the pipe

- viscosity

- pipe surface roughness

An increase in any one of these parameters will increase friction.

The amount of energy required to overcome the total friction loss within the system has to be supplied by the pump if you want to achieve the desired flow rate. In industrial systems, friction is not normally a large part of a pump's energy output. For typical systems, it is around 25% of the total. If it becomes much higher then you should examine the system to see if the pipes are too small. This is a guideline only, all pump systems are different. In some systems the friction energy may represent 100% of the pump's energy. This is what makes pump systems interesting, there is a million and one applications for them. In household systems, friction can be a greater proportion of the pump energy output, maybe up to 50% of the total, this is because small pipes have a proportionally higher friction than larger pipes for the same average fluid velocity in the pipe (see the friction chart later in this tutorial).

Another cause of friction are the fittings (elbows, tees, y's, etc) required to get the fluid from point A to B. Each one has a particular effect on the fluid streamlines. For example in the case of the elbow (see Figure 9), the fluid streamlines that are closest to the tight inner radius of the elbow lift off from the pipe surface forming small vortexes that consume energy. This energy loss is small for one elbow but if you have several elbows and other fittings it can become significant. Generally speaking they rarely represent more than 30% of the total friction due to the overall pipe length.

Figure 9 Streamline flow patterns for typical fittings such an elbow and a tee.

4. Flow rate depends on elevation difference

For identical systems, the flow rate will vary with the discharge pipe end elevation with respect to the suction tank fluid surface. If the pipe end elevation is high, the flow rate will be low (see Figure 10). Compare this to a cyclist on a hill with a slight upward slope, his velocity will be moderate and correspond to the amount of energy he can supply to overcome the friction of the wheels on the road and the change in elevation.

Figure 10 The effect of pipe end elevation on flow.

If the liquid surface of the suction tank is at the same elevation as the discharge end of the pipe then the static head will be zero and the flow rate will be limited by the friction in the system. This is equivalent of a cyclist on a flat road, his velocity depends on the amount of friction between the wheels and the road and the air resistance (see Figure 11).

Figure 11 Flow rate is limited by friction in the system when the static head is zero.

In Figure 12, the discharge pipe end is raised vertically until the flow stops, the pump cannot raise the fluid higher than this point and the discharge pressure is at its maximum. Similarly the cyclist applies maximum force to the pedals without getting anywhere.

Figure 12 High static head decreases flow rate.

If the discharge pipe end is lower than the liquid surface of the suction tank then the static head will be negative and the flow rate high (see Figure 13). If this difference is large it is possible that a pump is not required since the energy provided by this difference in elevation may be sufficient to move the fluid through the system without the use of a pump as in the case of a siphon (see the pump glossary). By analogy, as the cyclist comes down the hill he looses his stored elevation energy which is transformed progressively into velocity energy. The lower he is on the slope, the faster he goes.

Figure 13 Negative static head increase flow rate.

This is a good opportunity to introduce the concept of head. Pumps are most often rated in terms of head and flow. What is head? In Figure 12, the discharge pipe end is raised to a height at which the flow stops, measure the difference between that elevation and the surface of the suction tank and you obtain the head of the pump at zero flow. We measure this difference in height in feet (see Figure 13a). Head varies depending on flow rate, but in this case since there is no flow and hence no friction, the head of the pump is THE MAXIMUM FLUID SUPPORT HEIGHT.

Figure 13a Highest possible total head of a pump.

In this situation the pump will deliver its maximum pressure. If the pipe end is lowered as in Figure 10, the pump flow will increase and the head (also known as total head) will decrease to a value that corresponds to the flow. Why will the total head change depending on flow? If we start from the point of zero flow with the pipe end at its maximum elevation, the pipe end is lowered so that flow begins. If there is flow there must be friction, the friction energy is subtracted (because it is lost) from the maximum total head and the total head is reduced. At the same time the static head is reduced which further reduces the total head.

When you buy a pump you don’t specify the maximum total head that the pump can deliver since this occurs at zero flow. You instead specify the total head that occurs at your required flow rate. This head will depend on the maximum height you need to reach with respect to the suction tank fluid surface and the friction loss in your system.

For example, if your pump is supplying a bathtub on the 2nd floor, you will need enough head to reach that level, that will be your static head,  plus an additional amount to overcome the friction loss through the pipes and fittings. Assuming that you want to fill the bath as quickly as possible, then the taps on the bath will be fully open and will offer very little resistance or friction loss. If you want to supply a shower head for this bathtub then you will need a pump with more head for the same flow rate because the shower head is higher and offers more resistance than the bathtub taps.

Note: you can get more head from a pump by increasing it’s speed or it’s impeller diameter or both. In practice, home owners cannot make these changes and to obtain a higher total head, a new pump must be purchased.

5. Flow rate depends on friction

For identical systems, the flow rate will vary with the size and diameter of the discharge pipe. A system with a discharge pipe that is generously sized will have a high flow rate. This is what happens when you use a large drain pipe on a tank to be emptied, it drains very fast.

Figure 14 A large pipe produces low friction.

The smaller the pipe, the less the flow. How does the pump adjust itself to the diameter of the pipe, after all it does not know what size pipe will be installed? The pump you install is designed to produce a certain average flow for systems that have their pipes sized correspondingly. If you attempt to push that same flow through a small pipe the discharge pressure will increase and the flow will drop. Similarly if you try to empty a tank with a small tube, it will take a long time to drain (see Figure 15).

Figure 15 A small pipe produces high friction.

If the pipe is short the friction will be low and the flow rate high (see Figure 16)

Figure 16 A short pipe produces low friction.

and when the discharge pipe is long, the friction will be high and the flow rate low (see Figure 17).

Figure 17 A long pipe produced high friction.

Later on in the tutorial, a chart will be presented giving the size of pipes for various flow rates.

6. How does a centrifugal pump produce pressure

Fluid particles enter the pump at the suction flange or connection. They then turn 90 degrees into the plane of the impeller and fill up the volume between each impeller vane. The following fixed image shows what happens to the fluid particles from that point forward (for an animated version go to www.fluidedesign.com/downloads.htm in the middle of the page).

Figure 18 Fluid particle paths in a centrifugal pump.

Figure 19 Different parts of a centrifugal pump.

Figure 19a Cut-away view of centrifugal pump parts.

A more detail look at a more realistic cross-section of a closed impeller pump can be seen in Figure 19a.

The rotational motion of the impeller projects fluid particles at high speed onto the fixed casing or volute. The fluid particles are then slowed down to the speed at which they leave the pump at the discharge connection (see Figures 18 and 19).

Moving fluid particles have velocity energy. What is velocity energy? It's a way to express how the velocity of objects can affect other objects, you for example. Have you ever been tackled in a football match? The velocity at which the other player comes at you determines how hard you are hit. The mass of the player is also an important factor. The combination of mass and velocity produces velocity energy. Another example is catching a hard baseball pitch, ouch, there can be allot of velocity in a small fast moving baseball. Fluid particles that move at high speed have velocity energy, just put your hand on the open end of a garden hose.

The fluid particles in the pump are expelled from the tips of the impeller vanes at high velocity, they then slow down as they get closer to the discharge connection, loosing some of their velocity energy. This decrease in velocity energy increases pressure energy. Unlike friction which wastes energy, the decrease in velocity energy serves to increase pressure energy, this is the principal of energy conservation in action. The same thing happens to a cyclist that starts at the top of a hill, his speed gradually increases as he looses elevation. In that case, the cyclist’s elevation energy was transformed into velocity energy, in the pump’s case it is the velocity energy that is transformed into pressure energy.

Try this experiment, find a plastic cup or other container that you can poke a small pinhole in the bottom. Fill it with water and attach a string to it, and now you guessed it, start spinning it.

Figure 20 An experiment with centrifugal force.

The faster you spin, the more water comes out the small hole, the water is pressurized inside the cup using centrifugal force, just like a pump.

Previously we discussed how the flow rate changes with a change of the discharge pipe end elevation or changes due to an increase or decrease in pipe friction. This causes the pressure at the pump outlet to increase if the flow drops and decrease if the flow increases, sounds backwards doesn’t it. Well it’s not and you will see why. How does the pump adjust to this change in pressure. Or in other words, if the pressure changes due to outside factors, how does the pump respond to this change.

Pressure is produced by the rotational speed of the impeller vanes. The speed is constant. The pump will produce a certain discharge pressure corresponding to the particular conditions of the system (for example, fluid viscosity, pipe size, elevation difference, etc.). If changing something in the system causes the flow to decrease (for example closing a discharge valve), there will be an increase in pressure at the pump discharge because there is no corresponding reduction in the impeller speed. The pump produces excess velocity energy because it runs at constant speed, the excess velocity energy is transformed into pressure energy and the pressure goes up.

All centrifugal pumps have a performance or characteristic curve that looks something like the one shown in Figure 21 (assuming that the level in the suction tank remains constant), this shows how the discharge pressure varies with the flow rate through the pump.

Figure 21 Typical curve of discharge pressure vs. flow rate for a pump.

At 200 gpm, this pump produces 20 psig discharge pressure, and as the flow drops the pressure increases, and will be 40 psig at zero flow.

Note: this applies to centrifugal pumps, many home owners have positive displacement pumps, often piston pumps. These pumps produce constant flow no matter what changes are made to the system.

7. What can affect the discharge pressure of the pump?

Discharge elevation is not the only elevation that affects pump pressure and flow. What about the suction side of the pump? The difference in elevation between the suction tank fluid surface and the discharge pipe end is known as the STATIC HEAD. The difference between Figure 22 and 23 is the static head is a smaller in Figure 22. If everything else is the same, the pump in Figure 22 will produce more flow. The reason is that the pump in Figure 23 must produce more pressure at its discharge to displace the fluid to the higher elevation, more pressure implies less flow.

The pump will provide the energy to overcome friction of the moving fluid and the work or energy required to raise the fluid from the surface of the suction tank to the height of the discharge pipe end. If that height is 20 feet, then the static head is 20 feet.

Figure 22 The effect of static head on flow rate.

Figure 23 The effect of increasing the static head on flow rate.

Sometimes the discharge pipe end is submerged such as in Figure 24, then the static head will be the difference in elevation between the discharge tank fluid surface and suction tank fluid surface. The fluid particles will get to the discharge tank fluid surface therefore the pump must provide the energy to get to that level. Avoid making the mistake of using the discharge pipe end as the elevation for calculating static head if the end is submerged.

Note: if the discharge pipe end is submerged then a check valve on the pump discharge is required to avoid backflow when the pump is stopped

Figure 24 The height of the discharge pipe end does not influence the static head.

Figure 24a Incorrect difference in elevation for static head.

The static head can be changed by raising the surface of the discharge tank (assuming the pipe end is submerged) or suction tank or both. All of these changes will influence the flow rate.

8. Is more pressure better? Depends.

If the flow rate of your pump system is insufficient, the first reaction may be to buy a bigger pump. Depending on the cost, this is an option. However, the problem may be due to small or plugged pipes. Buying another pump without examining the system is a hit or miss proposition. Which leads us into the next topic, how to select a centrifugal pump.

9. How to select a centrifugal pump

It is unlikely that you can buy a centrifugal pump off the shelf, install it in an existing system and expect it to deliver exactly the flow rate you require. The flow rate that you obtain depends on the physical characteristics of your system such as friction which depends on the length and size of the pipes and elevation difference which depends on the building and location. The pump manufacturer has no means of knowing what these will be. This is why buying a centrifugal pump is more complicated than buying a positive displacement pump which will provide its rated flow no matter what system you install it in.

The main factors that affect the flow rate of a centrifugal pump are:

- friction, which depends on the length of pipe and the diameter

- static head, which depends on the difference of the pipe end discharge height vs. the suction tank fluid surface height

- fluid viscosity, if the fluid is different than water.

First, determine the flow rate. If you are a home owner, find out which of your uses for water is the biggest consumer. In many cases, this will be the bath which requires approximately 10 gpm (0.6 L/s). In an industrial setting, the flow rate will often depend on the production level of the plant. Selecting the right flow rate may be as simple as determining that it takes 100 gpm (6.3 L/s) to fill a tank in a reasonable amount of time or the flow rate may depend on the interaction between processes.

Second, determine the total head requirement of the pump. Total head is related to the discharge pressure of the pump. Why can't we just use discharge pressure? Pressure is a familiar concept, we are familiar with it in our daily lives. For example, fire extinguishers are pressurized at 60 psig (414 kPa), we put 35 psig (241 kPa) air pressure in our bicycle and car tires.

The main problem is from the manufacturer's point of view, he doesn't know how you will use the pump. The discharge pressure will also depend on the pressure available on the suction side of the pump. If your source of water for the pump is below of above the pump suction, for the same flow rate you will get a different discharge pressure. Therefore to eliminate this problem, it is preferable to use the difference in pressure between the inlet and outlet of the pump.

Pump manufacturers have taken this a step further, the amount of pressure that a pump can produce will depend on the density of the fluid, for a salt water solution which is denser than pure water, the pressure will be higher for the same flow rate. Once again, the manufacturer doesn't know what type of fluid is in your system, so that a criteria that does not depend on density is very useful. There is such a criteria and it is called TOTAL HEAD, it is the difference in head between the inlet and outlet of the pump.

You can measure the discharge head by attaching a tube to the discharge side of the pump and measuring the height of the liquid in the tube with respect to the suction of the pump. If the fluid is water the tube will have to be quite high. Mercury can be substituted for water to make the tube a reasonable length since mercury is 14 times heavier than water. You can do the same to measure the suction head. The difference between the two is the total head of the pump.

Figure 25 How total head can be measured.

The fluid in the measuring tube of the discharge or suction side of the pump will rise to the same height as water regardless of its density. This is because head is independent of density. If you convert head to pressure or difference in pressure between discharge and suction then yes the pressure will be greater for the denser fluid. Pressure will always be greater for the denser fluid because converting head to pressure requires the density of the fluid. For example, a denser fluid weighs more so that there will be a greater pressure at the bottom of a tank as compared to a tank filled with water at the same height.

So for these reasons the pump manufacturers have chosen total head as the main parameter that describes the pump’s available energy.

10. What is total head?

Total head is the difference in pressure between the outlet and the inlet of the pump converted to head since a pump’s main energy output is pressure energy. Head is also the amount of energy spent per unit weight of fluid displaced. As stated previously, the amount of energy that the pump must produce will depend mainly on how much friction and elevation difference or static head is present.

What is the unit of head? First let's deal with the unit of energy. Energy can be expressed in foot-pounds which is the amount of force required to lift an object up multiplied by the vertical distance. A good example is weight lifting. If you lift 100 pounds (445 N) up 6 feet (1.83 m), the energy required is 6 x 100= 600 ft-lbf (814 N-m). Or in terms of head, the energy divided by the weight displaced is 6 x 100 / 100= 6 feet (1.83 m), so the amount of energy per pound of dumbbell that the weight lifter needs to provide is 6 feet. This is not terribly useful to know for a weight lifter but we will see how very useful it is for displacing fluids.

Figure 26 Energy is required to lift weights.

You may be interested to know that 324 foot-pounds of energy is equivalent to 1 calorie. This means that our weight lifter spends 600/324 = 1.8 calories each time he lifts that weight up 6 feet, not much is it.

The following figure shows how much energy is required to displace vertically one gallon of water.

Figure 27 Energy required to lift 1 gallon of water up 10 feet.

This next figure shows how much head is required to do the same job.

Figure 28 Head vs. energy.

If we use energy to describe how much work the pump needs to do to displace a certain quantity of liquid, we will need to know the weight. If we use head, we only need to know the vertical distance of movement. This is very useful for fluids because pumping is a continuous process, usually when you pump you leave the pump on for a long time, you don't worry about how many pounds of fluid have been displaced. What we are interested in is getting the desired flow rate.

The other very useful aspect of using head is that the elevation difference or static head (you can see why now it is called head) can be used directly as one part of the value of total head, the other part being friction head. If you need to pump water up from the ground floor to the second floor, or 15 feet up. How much static head is that? Remember that you must also take into consideration the level of the water in the suction tank. If the water level is 10 feet below the pump suction connection then the static head will be 10 + 15 = 25 feet. Therefore the total head will need to be at least 15 feet plus the friction head loss of the fluid moving through the pipes.

Figure 29 Static head.

11. What is friction head?

Friction head is the amount of energy loss due to friction caused by fluid movement through pipes and fittings. It takes a force to move the fluid against friction, in the same way that a force is required to lift a weight. As long as the force is exerted in the same direction as the opposing force, energy is expended. In the same way that head was calculated to lift a certain weight, the friction head is calculated with the force required to overcome friction times the displacement (pipe length) divided by the weight of fluid displaced. These calculations have been done for us. The following table provides this information.

Table 1

Table 1 gives the flow rate and the friction head loss for water being moved through pipes of different diameter at a velocity of 10 ft /s. I have chosen 10 ft/s because it is a typical value for velocity in pipes, it is not too large which would create allot of friction and not too small which would slow things down, it’s just right. Velocity depends on the flow rate and the pipe diameter, you will find friction loss charts for flow rates of 5 ft/s and 15 ft/s in Appendix A, imperial and metric. If you wish to do you own calculation of velocity, you can find out how in Appendix D.

If the velocity you are using is less than 10 ft/s then the friction loss will be less and if the velocity is higher the loss will be greater. A velocity of 10 ft/s is normal practice for sizing pipes on the discharge side of the pump. For the suction side of the pump, it is desirable to be more conservative and size pipes for a lower velocity, for example between 4 and 7 feet/second. This is why you normally see a bigger pipe size on the suction side of the pump than on the discharge. A rule of thumb is to make the suction pipe the same size or one size larger than the suction connection of the pump.

Those who would like to do pipe friction calculations will find the information in Appendix B and pipe fittings friction loss calculations are in Appendix C.

12. The performance or characteristic curve of the pump

The pump characteristic curve has a similar appearance to the previous curve of discharge pressure vs. flow (Figure 21). As I mentioned this is not a practical way of describing the performance because you would have to know the suction pressure used to generate the curve. Figure 30 shows what a typical total head vs. flow rate characteristic curve looks like. This is the type of curve that all pump manufacturers normally publish with each model pump at a given operating speed.

Not all manufacturers will provide you with the pump characteristic curve. However, the curve does exist and if you insist you can probably get it. Generally speaking the more you pay, the more technical information you get.

Figure 30 Characteristic curve of a pump.

# Example of total head calculation

# Sizing a pump for a home owner application

Experience tells me that to fill a bath up in a reasonable amount of time, a flow rate of 10 gpm is required. According to Table 1, the copper tubing size should be somewhere between 1/2" and 3/4", I choose 3/4". I will design my system so that from the pump there is a 3/4" copper tube main distributor, there will be a 3/4" take-off from this distributor on the ground floor to the second floor level where the bath is. On the suction, I will use a pipe diameter of 1”, the suction pipe is 30 ft long.

Figure 31 Typical domestic water system.

# Friction loss on discharge side

Table 1 shows that a the 3/4" tube has a friction loss of 0.69 feet per feet of pipe. In this case, the distances are 10 feet of run on the main distributor and another 20 feet off of the main distributor up to the bath, for a total length of 30 feet.  The friction loss in feet is then 30 x 0.69 = 21 feet. There is some friction loss in the fittings, let's assume that a conservative estimate is 30% of the pipe friction head loss, the fittings friction head loss is = 0.3 x 21 = 6.3 feet. The total friction loss for the discharge side is then 21 + 6.3 = 27.3 feet.

# Friction loss on suction side

Table 1 shows that a 1" tube has a friction loss of 0.48 feet per feet of pipe. In this case, the distance is 30 feet. The friction loss in feet is then 30 x 0.48 = 14.4 feet. There is some friction loss in the fittings, let's assume that a conservative estimate is 30% of the pipe friction head loss, the fittings friction head loss is = 0.3 x 14.4 = 4.3 feet. If there is a check valve on the suction line the friction loss of the check valve will have to be added to the friction loss of the pipe. A typical value of friction loss for a check valve is 5 feet. A jet pump does not require a check valve therefore I will assume there is no check valve on the suction of this system. The total friction loss for the suction side is then 14.4 + 4.3 =  18.7 feet.

The total friction loss for piping in the system is then 27.3 + 18.7 = 46 feet.

The static head as per Figure 31 is 35 feet. Therefore the total head is 35 + 46 = 81 feet. We can now go to the store and purchase a pump with at least 81 feet of total head at 10 gpm. Sometimes total head is called Total Dynamic Head (T.D.H.), it has the same meaning. The pump’s rating should be as close as possible to these two figures without splitting hairs. You can allow yourself a 30% variation on the upward side on the total head. On the flow, you can also allow a variation but you may wind up paying for more than what you need.

What is the pump rating? The manufacturer will rate the pump at its optimum total head and flow, this point is also known as the best efficiency point or B.E.P.. At that flow rate, the pump is at its most efficient and there will be minimal amount of vibration and noise.  Of course, the pump can operate at other flow rates, higher or lower than the rating but the life of the pump will suffer if you operate too far away from its normal rating. Therefore, as a guideline aim for a maximum variation of +30% on total head.

Figure 32 Best efficient point of a pump.

14. Calculate the pump discharge pressure from the pump total head

First we need to know what the relationship between pressure and head is. Or it would be more accurate to say the relationship between pressure and pressure head just like there is a relationship between elevation energy and static head. The relationship is:

Or If we need to calculate pressure from pressure head:

where H is the pressure head in feet of fluid, p is pressure in psi and SG is the specific gravity. SG is the ratio of the density of the fluid to the density of water at 60F. Therefore if the fluid is water, then SG = 1.

If we have the characteristic curve of the pump and we know the flow rate we can determine the total head of the pump.

Figure 33 Characteristic pump curve.

For example if the characteristic curve of the pump is as shown in Figure 33 and the flow in the system is 20 gpm. The total head is then 100 feet.

Further more, the installation is as shown in Figure 34 which is a domestic water system that takes its water from a shallow well 15 feet lower than the pump suction.

Figure 34 Typical pump system.

The pump will have to generate lift to get the water up to its suction connection. This means that the pressure will be negative (relative to atmosphere) at the pump suction. Since we know the total head from the characteristic curve, if we subtract that value from the pressure head at the suction we will get the pressure head at the discharge which we then convert to pressure. We know that the pump must generate 15 feet of lift at the pump suction, lift is negative static head. It should in fact be slightly more than 15 feet because a higher suction lift will be required due to friction. But let’s assume that the pipe is generously sized and that the friction loss is small.

TOTAL HEAD =  100 =  HD - HS

or

HD = 100 + HS

The total head is equal to the difference between the pressure head at the discharge HD and the pressure head at the suction HS. HS is equal to –15 feet because it is a lift therefore:

HD = 100 + (-15) = 85 feet

The discharge pressure will be:

Now you can check your pump to see if the measured discharge pressure matches the prediction. If not, there may be something wrong with your pump.

Note: you must be careful where you locate the pressure gauge, if it is much higher than the pump suction, say higher than 2 feet, you will read less pressure than actually is there at the pump. Also the difference in velocity head of the pump discharge vs. the suction should be accounted for but this is typically small.

## APPENDIX A

Flow rate and friction loss for different pipe sizes based on 5 ft/s velocity

Flow rate and friction loss for different pipe sizes based on 15 ft/s velocity

Flow rate and friction loss for different pipe sizes based on 4.5 m/s velocity

Flow rate and friction loss for different pipe sizes based on 1.5 m/s velocity

FRICTION HEAD LOSS FOR VARIOUS FLOW RATES

FRICTION HEAD LOSS FOR VARIOUS FLOW RATES

FRICTION HEAD LOSS FOR VARIOUS FLOW RATES

PIPE FRICTION HEAD LOSS FOR VARIOUS FLOW RATES

FRICTION HEAD LOSS FOR VARIOUS FLOW RATES

## APPENDIX B

Formulas and an example of how to do pipe friction calculations

PIPE FRICTION CALCULATION

The average velocity v in a pipe is calculated based on the formula [1] and the appropriate units are indicated in parentheses. (see the last page for a table of all the symbols)

|  |  | [1] |
| --- | --- | --- |

Or in the metric system

|  |  | [1a] |
| --- | --- | --- |

The Reynolds Re number is calculated based on formula [2].

|  |  | [2] |
| --- | --- | --- |

Or in the metric system

|  |  | [2a] |
| --- | --- | --- |

If the Reynolds number is below 2000 than the flow is said to be in a laminar regime. If the Reynolds number is above 4000 the regime is turbulent. The velocity is usually high enough in industrial processes and homeowner applications to make the flow regime turbulent. The viscosity of many fluids can be found in the Cameron Hydraulic data book. The viscosity of water at 60F is 1.13 cSt.

If the flow is laminar then the friction parameter f is calculated with the laminar flow equation [3].

|  |  | [3] |
| --- | --- | --- |

If the flow is turbulent then the friction parameter f is calculated based on the Swamee-Jain equation [4].

|  |  | [4] |
| --- | --- | --- |

In the turbulent flow regime the friction factor f depends on the absolute roughness of the pipe inner wall. Table B1 provide some values for various materials.

| PIPE MATERIAL | Absolute roughness ( (ft) |
| --- | --- |
| Steel or wrought iron | 0.00015 |
| Asphalt-dipped cast iron | 0.0004 |
| Galvanized iron | 0.0005 |
| Table B1 |

The friction factor (HFP/L is calculated with the Darcy-Weisback equation [5]

|  |  | [5] |
| --- | --- | --- |

g=32.17 ft/s2

or in the metric system

|  |  | [5a] |
| --- | --- | --- |

g=9.8 m/s2

The pipe friction loss (HFP is calculated with equation [6]

|  |  | [6] |
| --- | --- | --- |

or in the metric system

|  |  | [6a] |
| --- | --- | --- |

Example calculation

Calculate the pipe friction loss of a 2 1/12” schedule 40 (2.469” internal pipe diameter)  new steel pipe with a flow rate of 149 gpm for water at 60F and a pipe length of 50 feet. The roughness is 0.00015 ft and the viscosity is 1.13 cSt.

The average velocity v in the pipe is:

|  |  | [1’] |
| --- | --- | --- |

The Reynolds Re number is:

|  |  | [2’] |
| --- | --- | --- |

The friction parameter f is:

|  |  | [4’] |
| --- | --- | --- |

The friction factor (HFP/L is calculated with the Darcy-Weisback equation [5]

|  |  | [5’] |
| --- | --- | --- |

The pipe friction loss (HFP is:

|  |  | [6’] |
| --- | --- | --- |

# Symbols

| Variable nomenclature | Imperial system (FPS units) |
| --- | --- |
| D pipe diameter | in (inch) |
| Re Reynolds number | non dimensional |
| q flow rate | USgpm (gallons per minute) |
| (HFP friction head loss in pipes | ft (feet) |
| ( viscosity | CSt (centistokes) |
| ( pipe roughness | Ft (feet) |
| v velocity | ft/s (feet/second) |
| L pipe length | ft (feet) |
| f friction parameter | Non dimensional |
| (HFP/L friction factor | feet of fluid/100 ft of pipe |
| g acceleration due to gravity (32.17 ft/s2) | ft/s2 (feet per second square) |

## APPENDIX C

Formulas and an example of how to do pipe fittings friction calculations

PIPE FITTING FRICTION CALCULATION

The friction loss for fittings depends on a K factor which can be found in many sources such as the Cameron Hydraulic data book or the Hydraulic Institute Engineering data book, the charts which I reproduce here are shown Figures C1 and C2.

The fittings friction (HFF can be calculated based on the following formula where K is a factor dependant on the type of fitting, v is the velocity in feet/second, g is the acceleration due to gravity (32.17 ft/s2 or 9.8 m/s2).

In the metric system

For example a 2 ½” inch screwed elbow has a K factor of 0.85 according to Figure C1 and using a velocity of 10 ft/s (this is determined from the flow rate). The fittings friction loss will be:

Figure C1 Pressure head loss K coefficients for fittings (source the Hydraulic Institute Standards book www.pumps.org).

Figure C2 Pressure head loss K coefficients for manual valves and other devices (source the Hydraulic Institute Standards book www.pumps.org).

## APPENDIX D

Formula and an example of how to do velocity calculation for fluid flow in a pipe

PIPE AVERAGE VELOCITY CALCULATION

The average velocity in a pipe can be calculated based on the following formula where v is the velocity in feet/second, D the internal diameter in inches and q the flow rate in USgallons per minute.

In the metric system:

For example a 2 ½” inch schedule 40 pipe has an internal diameter of 2.469 in, what is the average pipe velocity for a flow rate of 105 gpm.

## APPENDIX E

The relationship between pressure and pressure head

THE RELATIONSHIP BETWEEN PRESSURE HEAD AND PRESSURE

When people talk about head they usually mean pressure head. Head means energy per unit weight and is also called specific energy. There are many types of energy: elevation, velocity, friction. All these have a corresponding head.

Pressure energy is equal to the pressure times the volume of liquid displaced or pV. Why is pV energy?

Pressure is a force divided by an area.

The volume is equal to the pipe length times the cross-sectional area.

Figure E1

Therefore

pV is an expression of energy because it represents a force times a distance. Similar to a weight lifter using force to displace a weight vertically.

Pressure head is pressure energy divided by the weight of fluid displaced. I call pressure head H:

W/V or weight divided by volume is the density of the fluid and is often expressed by the greek letter (.  If we use the units of psi for pressure and lbf/ft3 for density ((). Then:

Instead of an absolute value for fluid density many people prefer to use specific gravity SG which is the ratio of the fluid to the density.

(F is the density of the fluid and (W is the density of water at 60(F which is equal to 62.34 lb/ft3.

Therefore pressure head then becomes:

or

In the metric system