## trial
power vs. static head for 3" pipe, optimal nozzle dia. max 1.5" dia.
q (Usgpm) | static head (ft) | pipe dia (in) | nozzle dia. (in) | HF (ft) | f coef. | Reynolds no. | pipe velocity (ft/s) | nozzle velocity based on friction (ft/s) | nozzle velocity (ft/s) | water jet power (kW) | power at turbine wheel (kW) | elec. cost per month | pipe length (ft) | turbine rpm | turbine dia.
200 | 10 | 3 | 1.5 | 9.9175 | 0.019358 | 210943.9533 | 9.0778 | 2.3037 | 36.3111 | 0.77238 | 0.34757 | 17.5175 | 100 | 1040.3133 | 4
100 | 10 | 3 | 1.5 | 2.652 | 0.020706 | 105471.9767 | 4.5389 | 21.7432 | 18.1556 | 0.096547 | 0.043446 | 2.1897 | 100 | 520.1567 | 4
114 | 10 | 3 | 1.5 | 3.3962 | 0.020403 | 120238.0534 | 5.1743 | 20.6128 | 20.6973 | 0.14304 | 0.064367 | 3.2441 | 100 | 592.9786 | 4
Note: the calculations are a result of an iterative process, the flow number in column A must be changed up or down such that the velocity that corresponds to friction in column I is equal to the velocity that corresponds to flow in column J

## 100 feet
power vs. static head for 2" pipe, optimal nozzle dia. max 1.5" dia.
q (Usgpm) | static head (ft) | pipe dia (in) | no. of nozzles | nozzle dia. (in) | HF (ft) | f coef. | Reynolds no. | pipe velocity (ft/s) | nozzle velocity based on friction (ft/s) | nozzle velocity (ft/s) | water jet power (W) | power at turbine wheel (W) | elec. cost per month | pipe length (ft) | turbine rpm | turbine dia.
61 | 10 | 2 | 1 | 1.5 | 7.9862 | 0.022067 | 96506.8586 | 6.2296 | 11.3828 | 11.0749 | 21.9143 | 9.8614 | 0.49702 | 100 | 317.2956 | 4
88 | 20 | 2 | 1 | 1.5 | 16.0751 | 0.021343 | 139223.0092 | 8.987 | 15.8912 | 15.9769 | 65.794 | 29.6073 | 1.4922 | 100 | 457.7379 | 4
108 | 30 | 2 | 1 | 1.5 | 23.8364 | 0.021012 | 170864.6022 | 11.0295 | 19.914 | 19.608 | 121.6213 | 54.7296 | 2.7584 | 100 | 561.7692 | 4
125 | 40 | 2 | 1 | 1.5 | 31.6145 | 0.020803 | 197759.9562 | 12.7656 | 23.2276 | 22.6944 | 188.5682 | 84.8557 | 4.2767 | 100 | 650.1958 | 4
140 | 50 | 2 | 1 | 1.5 | 39.3775 | 0.020657 | 221491.151 | 14.2975 | 26.1428 | 25.4178 | 264.9248 | 119.2161 | 6.0085 | 100 | 728.2193 | 4
power vs. static head for 3" pipe, optimal nozzle dia. max 1.5" dia.
q (Usgpm) | static head (ft) | pipe dia (in) | no. of nozzles | nozzle dia. (in) | HF (ft) | f coef. | Reynolds no. | pipe velocity (ft/s) | nozzle velocity based on friction (ft/s) | nozzle velocity (ft/s) | water jet power (kW) | power at turbine wheel (kW) | elec. cost per month | pipe length (ft) | turbine rpm | turbine dia.
114 | 10 | 3 | 1 | 1.5 | 3.3962 | 0.020403 | 120238.0534 | 5.1743 | 20.6128 | 20.6973 | 143.0385 | 64.3673 | 3.2441 | 100 | 592.9786 | 4
162 | 20 | 3 | 1 | 1.5 | 6.6236 | 0.019705 | 170864.6022 | 7.353 | 29.3366 | 29.412 | 410.472 | 184.7124 | 9.3095 | 100 | 842.6538 | 4
195 | 30 | 3 | 1 | 1.5 | 9.4469 | 0.019397 | 205670.3545 | 8.8508 | 36.3646 | 35.4033 | 715.8834 | 322.1475 | 16.2362 | 100 | 1014.3055 | 4
230 | 40 | 3 | 1 | 1.5 | 12.9777 | 0.019154 | 242585.5463 | 10.4394 | 41.6967 | 41.7578 | 1174.6865 | 528.6089 | 26.6419 | 100 | 1196.3603 | 4
260 | 50 | 3 | 1 | 1.5 | 16.4428 | 0.018991 | 274227.1393 | 11.8011 | 46.4658 | 47.2044 | 1696.9088 | 763.609 | 38.4859 | 100 | 1352.4073 | 4
340 | 75 | 3 | 1 | 1.5 | 27.659 | 0.018681 | 358604.7207 | 15.4322 | 55.1899 | 61.7289 | 3794.6804 | 1707.6062 | 86.0634 | 100 | 1768.5327 | 4
405 | 100 | 3 | 1 | 1.5 | 38.8855 | 0.01851 | 427161.5055 | 18.3825 | 62.7065 | 73.53 | 6413.6245 | 2886.131 | 145.461 | 100 | 2106.6345 | 4
power vs. static head for 4" pipe, optimal nozzle dia. max 1.5" dia.
q (Usgpm) | static head (ft) | pipe dia (in) | no. of nozzles | nozzle dia. (in) | HF (ft) | f coef. | Reynolds no. | pipe velocity (ft/s) | nozzle velocity based on friction (ft/s) | nozzle velocity (ft/s) | water jet power (W) | power at turbine wheel (kW) | elec. cost per month | pipe length (ft) | turbine rpm | turbine dia.
133 | 10 | 4 | 1 | 1.5 | 1.0786 | 0.020061 | 105208.2967 | 3.3957 | 23.9584 | 24.1469 | 227.1399 | 102.2129 | 5.1515 | 100 | 691.8084 | 4
185 | 20 | 4 | 1 | 1.5 | 2.0052 | 0.019277 | 146342.3676 | 4.7233 | 34.0262 | 33.5878 | 611.2989 | 275.0845 | 13.8643 | 100 | 962.2898 | 4
235 | 30 | 4 | 1 | 1.5 | 3.1552 | 0.018798 | 185894.3589 | 5.9998 | 41.5595 | 42.6656 | 1252.974 | 563.8383 | 28.4174 | 100 | 1222.3682 | 4
265 | 40 | 4 | 1 | 1.5 | 3.9664 | 0.018583 | 209625.5536 | 6.7658 | 48.1498 | 48.1122 | 1796.7021 | 808.516 | 40.7492 | 100 | 1378.4152 | 4
295 | 50 | 4 | 1 | 1.5 | 4.8682 | 0.018405 | 233356.7484 | 7.5317 | 53.8867 | 53.5589 | 2478.5889 | 1115.365 | 56.2144 | 100 | 1534.4622 | 4
364 | 75 | 4 | 1 | 1.5 | 7.2853 | 0.018091 | 287938.4963 | 9.2934 | 66.0058 | 66.0862 | 4656.3177 | 2095.343 | 105.6053 | 100 | 1262.2468 | 6
420 | 100 | 4 | 1 | 1.5 | 9.5978 | 0.017902 | 332236.7265 | 10.7231 | 76.2658 | 76.2533 | 7152.9688 | 3218.8359 | 162.2293 | 100 | 1456.4387 | 6
power vs. static head for 6" pipe, optimal nozzle dia. max 1.5" dia.
q (Usgpm) | static head (ft) | pipe dia (in) | no. of nozzles | nozzle dia. (in) | HF (ft) | f coef. | Reynolds no. | pipe velocity (ft/s) | nozzle velocity based on friction (ft/s) | nozzle velocity (ft/s) | water jet power (kW) | power at turbine wheel (kW) | elec. cost per month | pipe length (ft) | turbine rpm | turbine dia.
140 | 10 | 6 | 1 | 1.5 | 0.16052 | 0.020462 | 73830.3837 | 1.5886 | 25.1609 | 25.4178 | 264.9248 | 119.2161 | 6.0085 | 100 | 728.2193 | 4
195 | 20 | 6 | 1 | 1.5 | 0.29551 | 0.019417 | 102835.1772 | 2.2127 | 35.606 | 35.4033 | 715.8834 | 322.1475 | 16.2362 | 100 | 1014.3055 | 4
240 | 30 | 6 | 1 | 1.5 | 0.43447 | 0.018845 | 126566.372 | 2.7233 | 43.6148 | 43.5733 | 1334.6647 | 600.5991 | 30.2702 | 100 | 1248.376 | 4
275 | 40 | 6 | 1 | 1.5 | 0.56007 | 0.018503 | 145023.9679 | 3.1205 | 50.3743 | 49.9278 | 2007.8744 | 903.5435 | 45.5386 | 100 | 1430.4308 | 4
310 | 50 | 6 | 1 | 1.5 | 0.7009 | 0.018222 | 163481.5638 | 3.5176 | 56.3197 | 56.2822 | 2876.2295 | 1294.3033 | 65.2329 | 100 | 1612.4857 | 4
385 | 75 | 6 | 1 | 1.5 | 1.0536 | 0.01776 | 203033.5551 | 4.3687 | 68.9762 | 69.8989 | 5509.6073 | 2479.3233 | 124.9579 | 100 | 1335.0688 | 6
440 | 100 | 6 | 1 | 1.5 | 1.3562 | 0.017502 | 232038.3487 | 4.9928 | 79.6664 | 79.8844 | 8224.2535 | 3700.9141 | 186.5261 | 100 | 1525.7929 | 6
Note: the calculations are a result of an iterative process, the flow number in column A must be changed up or down such that the velocity that corresponds to friction in column J is equal to the velocity that corresponds to flow in column K

## 500 feet
500 feet, single nozzle
power vs. static head for 2" pipe, optimal nozzle dia.
q (Usgpm) | static head (ft) | pipe dia (in) | no. of nozzles | nozzle dia. (in) | HF (ft) | f coef. | Reynolds no. | pipe velocity (ft/s) | nozzle velocity based on friction (ft/s) | nozzle velocity (ft/s) | water jet power (W) | power at turbine wheel (W) | elec. cost per month | pipe length (ft) | turbine rpm | turbine dia.
22 | 25 | 2 | 1 | 0.5 | 5.9407 | 0.02524 | 34805.7523 | 2.2468 | 35.0182 | 35.948 | 83.2706 | 37.4718 | 1.8886 | 500 | 1029.9102 | 4
31 | 50 | 2 | 1 | 0.5 | 11.1937 | 0.023952 | 49044.4691 | 3.1659 | 49.9679 | 50.654 | 232.9746 | 104.8386 | 5.2839 | 500 | 1451.2371 | 4
38 | 75 | 2 | 1 | 0.5 | 16.3621 | 0.023301 | 60119.0267 | 3.8807 | 61.4228 | 62.092 | 429.1156 | 193.102 | 9.7323 | 500 | 1778.9358 | 4
44 | 100 | 2 | 1 | 0.5 | 21.5396 | 0.022879 | 69611.5046 | 4.4935 | 71.0503 | 71.896 | 666.1645 | 299.774 | 15.1086 | 500 | 1373.2136 | 6
54 | 150 | 2 | 1 | 0.5 | 31.6937 | 0.02235 | 85432.3011 | 5.5148 | 87.2458 | 88.236 | 1231.4159 | 554.1372 | 27.9285 | 500 | 1685.3076 | 6
power vs. static head for 3" pipe, optimal nozzle dia.
q (Usgpm) | static head (ft) | pipe dia (in) | no. of nozzles | nozzle dia. (in) | HF (ft) | f coef. | Reynolds no. | pipe velocity (ft/s) | nozzle velocity based on friction (ft/s) | nozzle velocity (ft/s) | water jet power (W) | power at turbine wheel (W) | elec. cost per month | pipe length (ft) | turbine rpm | turbine dia.
80 | 25 | 3 | 1 | 1 | 8.7218 | 0.02128 | 84377.5813 | 3.6311 | 32.3626 | 32.68 | 250.2496 | 112.6123 | 5.6757 | 500 | 936.282 | 4
113 | 50 | 3 | 1 | 1 | 16.7003 | 0.020423 | 119183.3336 | 5.1289 | 46.2872 | 46.1605 | 705.2431 | 317.3594 | 15.9949 | 500 | 1322.4983 | 4
138 | 75 | 3 | 1 | 1 | 24.3966 | 0.020004 | 145551.3278 | 6.2637 | 57.0598 | 56.373 | 1284.5197 | 578.0338 | 29.1329 | 500 | 1076.7243 | 6
161 | 100 | 3 | 1 | 1 | 32.7285 | 0.019716 | 169809.8824 | 7.3076 | 65.7894 | 65.7685 | 2039.7696 | 917.8963 | 46.262 | 500 | 1256.1783 | 6
197 | 150 | 3 | 1 | 1 | 48.1689 | 0.019381 | 207779.794 | 8.9416 | 80.9433 | 80.4745 | 3736.8199 | 1681.569 | 84.7511 | 500 | 1537.063 | 6
power vs. static head for 4" pipe, optimal nozzle dia.
q (Usgpm) | static head (ft) | pipe dia (in) | no. of nozzles | nozzle dia. (in) | HF (ft) | f coef. | Reynolds no. | pipe velocity (ft/s) | nozzle velocity based on friction (ft/s) | nozzle velocity (ft/s) | water jet power (W) | power at turbine wheel (W) | elec. cost per month | pipe length (ft) | turbine rpm | turbine dia.
175 | 25 | 4 | 1 | 1.5 | 9.0281 | 0.019398 | 138431.9694 | 4.468 | 32.0567 | 31.7722 | 517.4312 | 232.844 | 11.7353 | 500 | 910.2742 | 4
250 | 50 | 4 | 1 | 1.5 | 17.7473 | 0.018685 | 197759.9562 | 6.3828 | 45.5537 | 45.3889 | 1508.5457 | 678.8456 | 34.2138 | 500 | 1300.3917 | 4
306 | 75 | 4 | 1 | 1.5 | 26.1076 | 0.018347 | 242058.1865 | 7.8126 | 56.0869 | 55.556 | 2766.322 | 1244.8449 | 62.7402 | 500 | 1591.6794 | 4
355 | 100 | 4 | 1 | 1.5 | 34.7149 | 0.018126 | 280819.1379 | 9.0636 | 64.8108 | 64.4522 | 4319.4009 | 1943.7304 | 97.964 | 500 | 1231.0374 | 6
437 | 150 | 4 | 1 | 1.5 | 51.8097 | 0.017852 | 345684.4035 | 11.1572 | 79.4831 | 79.3398 | 8057.1745 | 3625.7285 | 182.7367 | 500 | 1136.5423 | 8
power vs. static head for 6" pipe, optimal nozzle dia. Max. 1.5" dia.
q (Usgpm) | static head (ft) | pipe dia (in) | no. of nozzles | nozzle dia. (in) | HF (ft) | f coef. | Reynolds no. | pipe velocity (ft/s) | nozzle velocity based on friction (ft/s) | nozzle velocity (ft/s) | water jet power (W) | power at turbine wheel (W) | elec. cost per month | pipe length (ft) | turbine rpm | turbine dia.
215 | 25 | 6 | 1 | 1.5 | 1.7706 | 0.01914 | 113382.3749 | 2.4397 | 38.6598 | 39.0344 | 959.5196 | 431.7838 | 21.7619 | 500 | 1118.3368 | 4
300 | 50 | 6 | 1 | 1.5 | 3.2956 | 0.018297 | 158207.965 | 3.4042 | 54.8176 | 54.4667 | 2606.767 | 1173.0452 | 59.1215 | 500 | 1560.47 | 4
370 | 75 | 6 | 1 | 1.5 | 4.8877 | 0.01784 | 195123.1568 | 4.1985 | 67.1642 | 67.1756 | 4890.3915 | 2200.6762 | 110.9141 | 500 | 1283.0531 | 6
425 | 100 | 6 | 1 | 1.5 | 6.35 | 0.017567 | 224127.9504 | 4.8226 | 77.6237 | 77.1611 | 7411.4852 | 3335.1684 | 168.0925 | 500 | 1473.7772 | 6
525 | 150 | 6 | 1 | 1.5 | 9.4826 | 0.017191 | 276863.9387 | 5.9573 | 95.0836 | 95.3167 | 13970.6421 | 6286.789 | 316.8542 | 500 | 1365.4113 | 8
1.5" nozzle
1.5" nozzle
Note: the calculations are a result of an iterative process, the flow number in column A must be changed up or down such that the velocity that corresponds to friction in column J is equal to the velocity that corresponds to flow in column K

## 1000 feet
power vs. static head for 2" pipe, optimal nozzle dia.
q (Usgpm) | static head (ft) | pipe dia (in) | nozzle dia. (in) | HF (ft) | f coef. | Reynolds no. | pipe velocity (ft/s) | nozzle velocity based on friction (ft/s) | nozzle velocity (ft/s) | water jet power (W) | power at turbine wheel (W) | elec. cost per month | pipe length (ft) | turbine rpm | turbine dia.
27 | 50 | 2 | 0.5 | 17.3293 | 0.024441 | 42716.1505 | 2.7574 | 45.8479 | 44.118 | 153.927 | 69.2671 | 3.4911 | 1000 | 1263.9807 | 4
34 | 75 | 2 | 0.5 | 26.5867 | 0.023647 | 53790.7081 | 3.4722 | 55.8114 | 55.556 | 307.3691 | 138.3161 | 6.9711 | 1000 | 1061.1196 | 6
40 | 100 | 2 | 0.5 | 36.0229 | 0.023149 | 63283.186 | 4.085 | 64.1583 | 65.36 | 500.4993 | 225.2247 | 11.3513 | 1000 | 1248.376 | 6
44 | 125 | 2 | 0.5 | 43.0793 | 0.022879 | 69611.5046 | 4.4935 | 72.6001 | 71.896 | 666.1645 | 299.774 | 15.1086 | 1000 | 1373.2136 | 6
48 | 150 | 2 | 0.5 | 50.746 | 0.022646 | 75939.8232 | 4.902 | 79.9125 | 78.432 | 864.8627 | 389.1882 | 19.6151 | 1000 | 1498.0512 | 6
56 | 200 | 2 | 0.5 | 67.9049 | 0.022263 | 88596.4604 | 5.719 | 92.19 | 91.504 | 1373.37 | 618.0165 | 31.148 | 1000 | 1747.7264 | 6
power vs. static head for 3" pipe, optimal nozzle dia.
q (Usgpm) | static head (ft) | pipe dia (in) | nozzle dia. (in) | HF (ft) | f coef. | Reynolds no. | pipe velocity (ft/s) | nozzle velocity based on friction (ft/s) | nozzle velocity (ft/s) | water jet power (W) | power at turbine wheel (W) | elec. cost per month | pipe length (ft) | turbine rpm | turbine dia.
96 | 50 | 3 | 1 | 24.5584 | 0.020806 | 101253.0976 | 4.3573 | 40.4588 | 39.216 | 432.4314 | 194.5941 | 9.8075 | 1000 | 1123.5384 | 4
120 | 75 | 3 | 1 | 37.4244 | 0.020291 | 126566.372 | 5.4467 | 49.1693 | 49.02 | 844.5925 | 380.0666 | 19.1554 | 1000 | 936.282 | 6
139 | 100 | 3 | 1 | 49.468 | 0.01999 | 146606.0476 | 6.3091 | 57.0196 | 56.7815 | 1312.6468 | 590.6911 | 29.7708 | 1000 | 1084.5267 | 6
156 | 125 | 3 | 1 | 61.6308 | 0.019773 | 164536.2836 | 7.0807 | 63.8527 | 63.726 | 1855.5698 | 835.0064 | 42.0843 | 1000 | 1217.1666 | 6
172 | 150 | 3 | 1 | 74.2722 | 0.019602 | 181411.7999 | 7.8069 | 69.802 | 70.262 | 2487.0747 | 1119.1836 | 56.4069 | 1000 | 1342.0042 | 6
198 | 200 | 3 | 1 | 97.2791 | 0.019374 | 208834.5138 | 8.987 | 81.2961 | 80.883 | 3794.0152 | 1707.3068 | 86.0483 | 1000 | 1544.8653 | 6
power vs. static head for 4" pipe, optimal nozzle dia.
q (Usgpm) | static head (ft) | pipe dia (in) | nozzle dia. (in) | HF (ft) | f coef. | Reynolds no. | pipe velocity (ft/s) | nozzle velocity based on friction (ft/s) | nozzle velocity (ft/s) | water jet power (W) | power at turbine wheel (W) | elec. cost per month | pipe length (ft) | turbine rpm | turbine dia.
175 | 50 | 4 | 1.25 | 18.0562 | 0.019398 | 138431.9694 | 4.468 | 45.335 | 45.752 | 1072.9453 | 482.8254 | 24.3344 | 1000 | 1310.7948 | 4
213 | 75 | 4 | 1.25 | 26.1806 | 0.018986 | 168491.4827 | 5.4382 | 56.045 | 55.6867 | 1934.6493 | 870.5922 | 43.8778 | 1000 | 1595.4245 | 4
247 | 100 | 4 | 1.25 | 34.688 | 0.018707 | 195386.8368 | 6.3062 | 64.8242 | 64.5757 | 3016.8541 | 1357.5843 | 68.4222 | 1000 | 1233.3955 | 6
278 | 125 | 4 | 1.25 | 43.4606 | 0.018502 | 219909.0714 | 7.0977 | 72.431 | 72.6803 | 4301.2811 | 1935.5765 | 97.5531 | 1000 | 1388.1941 | 6
305 | 150 | 4 | 1.25 | 51.889 | 0.018352 | 241267.1466 | 7.787 | 79.451 | 79.7392 | 5680.1913 | 2556.0861 | 128.8267 | 1000 | 1523.0187 | 6
351 | 200 | 4 | 1.25 | 67.9343 | 0.018142 | 277654.9786 | 8.9615 | 92.1797 | 91.7654 | 8657.3463 | 3895.8058 | 196.3486 | 1000 | 1752.7199 | 6
power vs. static head for 6" pipe, optimal nozzle dia.
q (Usgpm) | static head (ft) | pipe dia (in) | nozzle dia. (in) | HF (ft) | f coef. | Reynolds no. | pipe velocity (ft/s) | nozzle velocity based on friction (ft/s) | nozzle velocity (ft/s) | water jet power (W) | power at turbine wheel (W) | elec. cost per month | pipe length (ft) | turbine rpm | turbine dia.
290 | 50 | 6 | 1.5 | 6.1856 | 0.018376 | 152934.3662 | 3.2907 | 53.0944 | 52.6511 | 2354.683 | 1059.6074 | 53.4042 | 1000 | 1005.6362 | 6
360 | 75 | 6 | 1.5 | 9.2835 | 0.017897 | 189849.558 | 4.085 | 65.0246 | 65.36 | 4504.4934 | 2027.0221 | 102.1619 | 1000 | 1248.376 | 6
415 | 100 | 6 | 1.5 | 12.1406 | 0.017612 | 218854.3516 | 4.7091 | 75.1856 | 75.3456 | 6900.5348 | 3105.2406 | 156.5041 | 1000 | 1439.1001 | 6
464 | 125 | 6 | 1.5 | 14.9982 | 0.017405 | 244694.9859 | 5.2651 | 84.128 | 84.2418 | 9644.7816 | 4340.1517 | 218.7436 | 1000 | 1609.018 | 6
510 | 150 | 6 | 1.5 | 17.9477 | 0.01724 | 268953.5405 | 5.7871 | 92.1751 | 92.5933 | 12807.0465 | 5763.1709 | 290.4638 | 1000 | 1768.5327 | 6
585 | 200 | 6 | 1.5 | 23.3093 | 0.017017 | 308505.5318 | 6.6381 | 106.6221 | 106.21 | 19328.8518 | 8697.9833 | 438.3784 | 1000 | 2028.611 | 6
Note: the calculations are a result of an iterative process, the flow number in column A must be changed up or down such that the velocity that corresponds to friction in column J is equal to the velocity that corresponds to flow in column K

## 2000 feet
power vs. static head for 2" pipe, optimal nozzle dia.
q (Usgpm) | static head (ft) | pipe dia (in) | nozzle dia. (in) | HF (ft) | f coef. | Reynolds no. | pipe velocity (ft/s) | nozzle velocity based on friction (ft/s) | nozzle velocity (ft/s) | water jet power (W) | power at turbine wheel (W) | elec. cost per month | pipe length (ft) | turbine rpm | turbine dia.
17 | 50 | 2 | 0.375 | 14.8316 | 0.026383 | 26895.3541 | 1.7361 | 47.5682 | 49.3831 | 121.4298 | 54.6434 | 2.754 | 2000 | 1414.8261 | 4
20 | 75 | 2 | 0.375 | 19.9531 | 0.025644 | 31641.593 | 2.0425 | 59.5123 | 58.0978 | 197.7281 | 88.9776 | 4.4845 | 2000 | 1109.6676 | 6
24 | 100 | 2 | 0.375 | 27.8869 | 0.024889 | 37969.9116 | 2.451 | 68.1158 | 69.7173 | 341.6742 | 153.7534 | 7.7492 | 2000 | 1331.6011 | 6
27 | 125 | 2 | 0.375 | 34.6586 | 0.024441 | 42716.1505 | 2.7574 | 76.2402 | 78.432 | 486.4853 | 218.9184 | 11.0335 | 2000 | 1498.0512 | 6
29 | 150 | 2 | 0.375 | 39.5618 | 0.024183 | 45880.3098 | 2.9616 | 84.2947 | 84.2418 | 602.7989 | 271.2595 | 13.6715 | 2000 | 1206.7635 | 8
34 | 200 | 2 | 0.375 | 53.1734 | 0.023647 | 53790.7081 | 3.4722 | 97.1948 | 98.7662 | 971.4382 | 437.1472 | 22.0322 | 2000 | 1414.8261 | 8
power vs. static head for 3" pipe, optimal nozzle dia.
q (Usgpm) | static head (ft) | pipe dia (in) | nozzle dia. (in) | HF (ft) | f coef. | Reynolds no. | pipe velocity (ft/s) | nozzle velocity based on friction (ft/s) | nozzle velocity (ft/s) | water jet power (W) | power at turbine wheel (W) | elec. cost per month | pipe length (ft) | turbine rpm | turbine dia.
60 | 50 | 3 | 0.75 | 20.4165 | 0.02214 | 63283.186 | 2.7233 | 43.628 | 43.5733 | 333.6662 | 150.1498 | 7.5675 | 2000 | 1248.376 | 4
74 | 75 | 3 | 0.75 | 30.1578 | 0.021499 | 78049.2627 | 3.3588 | 53.7136 | 53.7404 | 625.9701 | 281.6866 | 14.197 | 2000 | 1026.4425 | 6
86 | 100 | 3 | 0.75 | 39.9481 | 0.021086 | 90705.8999 | 3.9034 | 62.159 | 62.4551 | 982.548 | 442.1466 | 22.2842 | 2000 | 1192.8926 | 6
97 | 125 | 3 | 0.75 | 50.084 | 0.02078 | 102307.8174 | 4.4027 | 69.4269 | 70.4436 | 1409.8524 | 634.4336 | 31.9755 | 2000 | 1345.4719 | 6
105 | 150 | 3 | 0.75 | 58.1507 | 0.020591 | 110745.5755 | 4.7658 | 76.8738 | 76.2533 | 1788.2422 | 804.709 | 40.5573 | 2000 | 1092.329 | 8
122 | 200 | 3 | 0.75 | 77.2299 | 0.020256 | 128675.8115 | 5.5374 | 88.8765 | 88.5991 | 2805.0327 | 1262.2647 | 63.6181 | 2000 | 1269.1823 | 8
power vs. static head for 4" pipe, optimal nozzle dia.
q (Usgpm) | static head (ft) | pipe dia (in) | nozzle dia. (in) | HF (ft) | f coef. | Reynolds no. | pipe velocity (ft/s) | nozzle velocity based on friction (ft/s) | nozzle velocity (ft/s) | water jet power (W) | power at turbine wheel (W) | elec. cost per month | pipe length (ft) | turbine rpm | turbine dia.
115 | 50 | 4 | 1 | 16.4455 | 0.020457 | 90969.5799 | 2.9361 | 46.4639 | 46.9775 | 743.3563 | 334.5103 | 16.8593 | 2000 | 897.2703 | 6
140 | 75 | 4 | 1 | 23.7444 | 0.019929 | 110745.5755 | 3.5744 | 57.4264 | 57.19 | 1341.1816 | 603.5317 | 30.418 | 2000 | 1092.329 | 6
163 | 100 | 4 | 1 | 31.5905 | 0.01956 | 128939.4915 | 4.1616 | 66.3435 | 66.5855 | 2116.7341 | 952.5303 | 48.0075 | 2000 | 1271.7831 | 6
182 | 125 | 4 | 1 | 38.8855 | 0.019312 | 143969.2481 | 4.6467 | 74.4352 | 74.347 | 2946.5761 | 1325.9592 | 66.8283 | 2000 | 1420.0277 | 6
200 | 150 | 4 | 1 | 46.473 | 0.019113 | 158207.965 | 5.1063 | 81.6145 | 81.7 | 3910.1506 | 1759.5678 | 88.6822 | 2000 | 1170.3525 | 8
232 | 200 | 4 | 1 | 61.5817 | 0.018822 | 183521.2394 | 5.9233 | 94.3707 | 94.772 | 6103.3384 | 2746.5023 | 138.4237 | 2000 | 1357.6089 | 8
power vs. static head for 6" pipe, optimal nozzle dia. 1.5" max. dia.
q (Usgpm) | static head (ft) | pipe dia (in) | nozzle dia. (in) | HF (ft) | f coef. | Reynolds no. | pipe velocity (ft/s) | nozzle velocity based on friction (ft/s) | nozzle velocity (ft/s) | water jet power (W) | power at turbine wheel (W) | elec. cost per month | pipe length (ft) | turbine rpm | turbine dia.
275 | 50 | 6 | 1.5 | 11.2014 | 0.018503 | 145023.9679 | 3.1205 | 49.963 | 49.9278 | 2007.8744 | 903.5435 | 45.5386 | 2000 | 1430.4308 | 4
340 | 75 | 6 | 1.5 | 16.6734 | 0.018018 | 179302.3603 | 3.8581 | 61.2596 | 61.7289 | 3794.6804 | 1707.6062 | 86.0634 | 2000 | 1179.0218 | 6
390 | 100 | 6 | 1.5 | 21.5918 | 0.017734 | 205670.3545 | 4.4254 | 71.0266 | 70.8067 | 5727.0672 | 2577.1802 | 129.8899 | 2000 | 1352.4073 | 6
442 | 125 | 6 | 1.5 | 27.3578 | 0.017494 | 233093.0684 | 5.0155 | 79.2609 | 80.2476 | 8336.9129 | 3751.6108 | 189.0812 | 2000 | 1532.7283 | 6
480 | 150 | 6 | 1.5 | 31.9898 | 0.017345 | 253132.744 | 5.4467 | 87.1366 | 87.1467 | 10677.3178 | 4804.793 | 242.1616 | 2000 | 1664.5013 | 6
555 | 200 | 6 | 1.5 | 42.1652 | 0.017101 | 292684.7353 | 6.2977 | 100.7725 | 100.7633 | 16505.0714 | 7427.2821 | 374.335 | 2000 | 1924.5797 | 6
Note: the calculations are a result of an iterative process, the flow number in column A must be changed up or down such that the velocity that corresponds to friction in column I is equal to the velocity that corresponds to flow in column J

## 2 nozzles
500 feet, 2 nozzles
power vs. static head for 2" pipe, (2) optimum nozzle dia.
q (Usgpm) | static head (ft) | pipe dia (in) | no. of nozzles | nozzle dia. (in) | HF (ft) | f coef. | Reynolds no. | pipe velocity (ft/s) | nozzle velocity based on friction (ft/s) | single nozzle velocity (ft/s) | water jet power (1) nozzle (W) | power at turbine wheel (W) | % power increase compared to 1 nozzle | elec. cost per month | pipe length (ft) | turbine rpm | turbine dia. | turbine rpm increase %
34 | 25 | 2 | 2 | 0.5 | 13.2933 | 0.023647 | 53790.7081 | 3.4722 | 27.4446 | 27.778 | 38.4211 | 34.579 | -7.72% | 1.7428 | 500 | 795.8397 | 4 | -22.73%
48 | 50 | 2 | 2 | 0.5 | 25.373 | 0.022646 | 75939.8232 | 4.902 | 39.8058 | 39.216 | 108.1078 | 97.2971 | -7.193% | 4.9038 | 500 | 1123.5384 | 4 | -22.58%
60 | 75 | 2 | 2 | 0.5 | 38.6975 | 0.022104 | 94924.779 | 6.1275 | 48.3291 | 49.02 | 211.1481 | 190.0333 | -1.589% | 9.5777 | 500 | 1404.423 | 4 | -21.05%
69 | 100 | 2 | 2 | 0.5 | 50.4806 | 0.021803 | 109163.4959 | 7.0466 | 56.4454 | 56.373 | 321.1299 | 289.0169 | -3.588% | 14.5665 | 500 | 1076.7243 | 6 | -21.59%
85 | 150 | 2 | 2 | 0.5 | 75.203 | 0.021404 | 134476.7703 | 8.6806 | 69.3718 | 69.445 | 600.3303 | 540.2973 | -2.498% | 27.231 | 500 | 1326.3995 | 6 | -21.3%
power vs. static head for 3" pipe, (2) optimum nozzle dia.
q (Usgpm) | static head (ft) | pipe dia (in) | no. of nozzles | nozzle dia. (in) | HF (ft) | f coef. | Reynolds no. | pipe velocity (ft/s) | nozzle velocity based on friction (ft/s) | single nozzle velocity (ft/s) | water jet power (1) nozzle (W) | power at turbine wheel (W) | % power increase compared to 1 nozzle | elec. cost per month | pipe length (ft) | turbine rpm | turbine dia. | turbine rpm increase %
67 | 25 | 3 | 2 | 0.625 | 6.265 | 0.021793 | 70666.2244 | 3.0411 | 34.719 | 35.033 | 120.4253 | 108.3828 | -3.756% | 5.4625 | 500 | 1003.6943 | 4 | 7.2%
95 | 50 | 3 | 2 | 0.625 | 12.0397 | 0.020831 | 100198.3778 | 4.3119 | 49.4203 | 49.6736 | 343.2925 | 308.9632 | -2.646% | 15.5717 | 500 | 1423.1486 | 4 | 7.611%
115 | 75 | 3 | 2 | 0.625 | 17.2638 | 0.020384 | 121292.7732 | 5.2197 | 60.9487 | 60.1312 | 608.9575 | 548.0617 | -5.185% | 27.6223 | 500 | 1148.5059 | 6 | 6.667%
135 | 100 | 3 | 2 | 0.625 | 23.3982 | 0.020048 | 142387.1685 | 6.1275 | 70.2037 | 70.5888 | 985.1327 | 886.6194 | -3.407% | 44.6856 | 500 | 1348.2461 | 6 | 7.329%
165 | 150 | 3 | 2 | 0.625 | 34.2996 | 0.019673 | 174028.7615 | 7.4892 | 86.2796 | 86.2752 | 1798.6442 | 1618.7798 | -3.734% | 81.5865 | 500 | 1647.8563 | 6 | 7.208%
power vs. static head for 4" pipe, (2) optimum nozzle dia.
q (Usgpm) | static head (ft) | pipe dia (in) | no. of nozzles | nozzle dia. (in) | HF (ft) | f coef. | Reynolds no. | pipe velocity (ft/s) | nozzle velocity based on friction (ft/s) | single nozzle velocity (ft/s) | water jet power (1) nozzle (W) | power at turbine wheel (W) | % power increase compared to 1 nozzle | elec. cost per month | pipe length (ft) | turbine rpm | turbine dia. | turbine rpm increase %
162 | 25 | 4 | 2 | 1 | 7.8067 | 0.019574 | 128148.4517 | 4.1361 | 33.2598 | 33.0885 | 259.7518 | 233.7766 | 0.4005% | 11.7823 | 500 | 947.9855 | 4 | 4.143%
230 | 50 | 4 | 2 | 1 | 15.1442 | 0.018838 | 181939.1597 | 5.8722 | 47.3563 | 46.9775 | 743.3563 | 669.0207 | -1.447% | 33.7186 | 500 | 1345.9054 | 4 | 3.5%
285 | 75 | 4 | 2 | 1 | 22.7877 | 0.018461 | 225446.3501 | 7.2764 | 57.9598 | 58.2112 | 1414.3213 | 1272.8892 | 2.253% | 64.1536 | 500 | 1667.7523 | 4 | 4.779%
330 | 100 | 4 | 2 | 1 | 30.173 | 0.018232 | 261043.1423 | 8.4253 | 67.0274 | 67.4025 | 2195.6106 | 1976.0496 | 1.663% | 99.5929 | 500 | 1287.3878 | 6 | 4.577%
405 | 150 | 4 | 2 | 1 | 44.7382 | 0.017948 | 320371.1291 | 10.3402 | 82.2955 | 82.7212 | 4058.6217 | 3652.7596 | 0.7455% | 184.0991 | 500 | 1184.9819 | 8 | 4.262%
power vs. static head for 6" pipe, (2) 0.5" dia. Nozzle
q (Usgpm) | static head (ft) | pipe dia (in) | no. of nozzles | nozzle dia. (in) | HF (ft) | f coef. | Reynolds no. | pipe velocity (ft/s) | nozzle velocity based on friction (ft/s) | single nozzle velocity (ft/s) | water jet power (1) nozzle (W) | power at turbine wheel (W) | % power increase compared to 1 nozzle | elec. cost per month | pipe length (ft) | turbine rpm | turbine dia. | turbine rpm increase %
390 | 25 | 6 | 2 | 1.5 | 5.398 | 0.017734 | 205670.3545 | 4.4254 | 35.5133 | 35.4033 | 715.8834 | 644.2951 | 49.22% | 32.4725 | 500 | 1014.3055 | 4 | -9.302%
555 | 50 | 6 | 2 | 1.5 | 10.5413 | 0.017101 | 292684.7353 | 6.2977 | 50.3862 | 50.3817 | 2063.1339 | 1856.8205 | 58.29% | 93.5838 | 500 | 1443.4347 | 4 | -7.5%
680 | 75 | 6 | 2 | 1.5 | 15.5408 | 0.016794 | 358604.7207 | 7.7161 | 61.8515 | 61.7289 | 3794.6804 | 3415.2124 | 55.19% | 172.1267 | 500 | 1179.0218 | 6 | -8.108%
790 | 100 | 6 | 2 | 1.5 | 20.7236 | 0.016593 | 416614.3078 | 8.9643 | 71.4188 | 71.7144 | 5950.1751 | 5355.1576 | 60.57% | 269.8999 | 500 | 1369.7459 | 6 | -7.059%
970 | 150 | 6 | 2 | 1.5 | 30.7818 | 0.016348 | 511539.0868 | 11.0068 | 87.5814 | 88.0544 | 11014.4717 | 9913.0246 | 57.68% | 499.6164 | 500 | 1261.3799 | 8 | -7.619%
increase is due to limit on nozzle size of 1.5" on the single nozzle case.
Note: the calculations are a result of an iterative process, the flow number in column A must be changed up or down such that the velocity that corresponds to friction in column J is equal to the velocity that corresponds to flow in column K

## 3 nozzles
500 feet, 3 nozzles
power vs. static head for 2" pipe, (3) optimum nozzle dia.
q (Usgpm) | static head (ft) | pipe dia (in) | no. of nozzles | nozzle dia. (in) | HF (ft) | f coef. | Reynolds no. | pipe velocity (ft/s) | nozzle velocity based on friction (ft/s) | single nozzle velocity (ft/s) | water jet power (1) nozzle (W) | power at turbine wheel (W) | % power increase compared to 1 nozzle | elec. cost per month | pipe length (ft) | turbine rpm | turbine dia. | turbine rpm increase %
31 | 25 | 2 | 3 | 0.375 | 11.1937 | 0.023952 | 49044.4691 | 3.1659 | 29.8043 | 30.0172 | 27.2709 | 36.8157 | -1.751% | 1.8555 | 500 | 859.9924 | 4 | -16.5%
44 | 50 | 2 | 3 | 0.375 | 21.5396 | 0.022879 | 69611.5046 | 4.4935 | 42.7918 | 42.605 | 77.9781 | 105.2704 | 0.4119% | 5.3056 | 500 | 1220.6343 | 4 | -15.89%
54 | 75 | 2 | 3 | 0.375 | 31.6937 | 0.02235 | 85432.3011 | 5.5148 | 52.7857 | 52.288 | 144.1438 | 194.5941 | 0.7727% | 9.8075 | 500 | 1498.0512 | 4 | -15.79%
63 | 100 | 2 | 3 | 0.375 | 42.455 | 0.021996 | 99671.0179 | 6.4339 | 60.8477 | 61.0027 | 228.895 | 309.0083 | 3.08% | 15.574 | 500 | 1165.1509 | 6 | -15.15%
77 | 150 | 2 | 3 | 0.375 | 62.2386 | 0.021586 | 121820.1331 | 7.8636 | 75.1437 | 74.5588 | 417.9139 | 564.1838 | 1.813% | 28.4349 | 500 | 1424.0734 | 6 | -15.5%
power vs. static head for 3" pipe, (3) optimum nozzle dia.
q (Usgpm) | static head (ft) | pipe dia (in) | no. of nozzles | nozzle dia. (in) | HF (ft) | f coef. | Reynolds no. | pipe velocity (ft/s) | nozzle velocity based on friction (ft/s) | single nozzle velocity (ft/s) | water jet power (1) nozzle (W) | power at turbine wheel (W) | % power increase compared to 1 nozzle | elec. cost per month | pipe length (ft) | turbine rpm | turbine dia. | turbine rpm increase %
65 | 25 | 3 | 3 | 0.5 | 5.9217 | 0.021886 | 68556.7848 | 2.9503 | 35.0356 | 35.4033 | 79.5426 | 107.3825 | -4.644% | 5.4121 | 500 | 1014.3055 | 4 | 8.333%
92 | 50 | 3 | 3 | 0.5 | 11.3348 | 0.020912 | 97034.2185 | 4.1758 | 49.877 | 50.1093 | 225.5398 | 304.4787 | -4.059% | 15.3457 | 500 | 1435.6324 | 4 | 8.555%
112 | 75 | 3 | 3 | 0.5 | 16.422 | 0.020443 | 118128.6139 | 5.0836 | 61.3914 | 61.0027 | 406.9244 | 549.348 | -4.963% | 27.6871 | 500 | 1165.1509 | 6 | 8.213%
130 | 100 | 3 | 3 | 0.5 | 21.7794 | 0.020124 | 137113.5697 | 5.9006 | 70.9416 | 70.8067 | 636.3408 | 859.0601 | -6.41% | 43.2966 | 500 | 1352.4073 | 6 | 7.66%
160 | 150 | 3 | 3 | 0.5 | 32.3414 | 0.019727 | 168755.1627 | 7.2622 | 87.0066 | 87.1467 | 1186.3686 | 1601.5977 | -4.756% | 80.7205 | 500 | 1664.5013 | 6 | 8.291%
power vs. static head for 4" pipe, (3) optimum nozzle dia.
q (Usgpm) | static head (ft) | pipe dia (in) | no. of nozzles | nozzle dia. (in) | HF (ft) | f coef. | Reynolds no. | pipe velocity (ft/s) | nozzle velocity based on friction (ft/s) | single nozzle velocity (ft/s) | water jet power (1) nozzle (W) | power at turbine wheel (W) | % power increase compared to 1 nozzle | elec. cost per month | pipe length (ft) | turbine rpm | turbine dia. | turbine rpm increase %
145 | 25 | 4 | 3 | 0.75 | 6.3395 | 0.019841 | 114700.7746 | 3.702 | 34.6499 | 35.1007 | 174.421 | 235.4683 | 1.127% | 11.8676 | 500 | 1005.6362 | 4 | 10.48%
205 | 50 | 4 | 3 | 0.75 | 12.1743 | 0.019063 | 162163.1641 | 5.2339 | 49.3326 | 49.6252 | 492.8971 | 665.4111 | -1.979% | 33.5367 | 500 | 1421.7616 | 4 | 9.333%
250 | 75 | 4 | 3 | 0.75 | 17.7473 | 0.018685 | 197759.9562 | 6.3828 | 60.693 | 60.5185 | 893.953 | 1206.8366 | -3.053% | 60.8246 | 500 | 1733.8556 | 4 | 8.932%
290 | 100 | 4 | 3 | 0.75 | 23.558 | 0.018433 | 229401.5493 | 7.4041 | 70.1304 | 70.2015 | 1395.3677 | 1883.7464 | -3.086% | 94.9408 | 500 | 1340.8483 | 6 | 8.92%
355 | 150 | 4 | 3 | 0.75 | 34.7149 | 0.018126 | 280819.1379 | 9.0636 | 86.1246 | 85.9363 | 2559.645 | 3455.5207 | -4.694% | 174.1582 | 500 | 1231.0374 | 8 | 8.314%
power vs. static head for 6" pipe, (3) optimum nozzle dia.
q (Usgpm) | static head (ft) | pipe dia (in) | no. of nozzles | nozzle dia. (in) | HF (ft) | f coef. | Reynolds no. | pipe velocity (ft/s) | nozzle velocity based on friction (ft/s) | single nozzle velocity (ft/s) | water jet power (1) nozzle (W) | power at turbine wheel (W) | % power increase compared to 1 nozzle | elec. cost per month | pipe length (ft) | turbine rpm | turbine dia. | turbine rpm increase %
400 | 25 | 6 | 3 | 1.25 | 5.6623 | 0.017684 | 210943.9533 | 4.5389 | 35.273 | 34.8587 | 474.5475 | 640.6391 | 48.37% | 32.2882 | 500 | 998.7008 | 4 | -10.7%
570 | 50 | 6 | 3 | 1.25 | 11.0911 | 0.017058 | 300595.1335 | 6.4679 | 50.0339 | 49.6736 | 1373.1698 | 1853.7792 | 58.03% | 93.4305 | 500 | 1423.1486 | 4 | -8.8%
700 | 75 | 6 | 3 | 1.25 | 16.4286 | 0.016754 | 369151.9183 | 7.9431 | 61.388 | 61.0027 | 2543.2778 | 3433.425 | 56.02% | 173.0446 | 500 | 1165.1509 | 6 | -9.189%
815 | 100 | 6 | 3 | 1.25 | 22.0035 | 0.016553 | 429798.3049 | 9.248 | 70.8399 | 71.0245 | 4013.955 | 5418.8393 | 62.48% | 273.1095 | 500 | 1356.5686 | 6 | -7.953%
1000 | 150 | 6 | 3 | 1.25 | 32.6483 | 0.016314 | 527359.8833 | 11.3472 | 86.8931 | 87.1467 | 7414.804 | 10009.9854 | 59.22% | 504.5033 | 500 | 1248.376 | 8 | -8.571%
increase is due to limit on nozzle size of 1.5" on the single nozzle case.
Note: the calculations are a result of an iterative process, the flow number in column A must be changed up or down such that the velocity that corresponds to friction in column J is equal to the velocity that corresponds to flow in column K

## 4 nozzles
500 feet, 4 nozzles
power vs. static head for 2" pipe, (4) optimum nozzle dia.
q (Usgpm) | static head (ft) | pipe dia (in) | no. of nozzles | nozzle dia. (in) | HF (ft) | f coef. | Reynolds no. | pipe velocity (ft/s) | nozzle velocity based on friction (ft/s) | single nozzle velocity (ft/s) | water jet power (1) nozzle (W) | power at turbine wheel (W) | % power increase compared to 1 nozzle | elec. cost per month | pipe length (ft) | turbine rpm | turbine dia. | turbine rpm increase %
22 | 25 | 2 | 4 | 0.25 | 5.9407 | 0.02524 | 34805.7523 | 2.2468 | 35.0182 | 35.948 | 20.8176 | 37.4718 | 0% | 1.8886 | 500 | 1029.9102 | 4 | 0%
31 | 50 | 2 | 4 | 0.25 | 11.1937 | 0.023952 | 49044.4691 | 3.1659 | 49.9679 | 50.654 | 58.2436 | 104.8386 | 0% | 5.2839 | 500 | 1451.2371 | 4 | 0%
38 | 75 | 2 | 4 | 0.25 | 16.3621 | 0.023301 | 60119.0267 | 3.8807 | 61.4228 | 62.092 | 107.2789 | 193.102 | 0% | 9.7323 | 500 | 1778.9358 | 4 | 0%
44 | 100 | 2 | 4 | 0.25 | 21.5396 | 0.022879 | 69611.5046 | 4.4935 | 71.0503 | 71.896 | 166.5411 | 299.774 | 0% | 15.1086 | 500 | 1373.2136 | 6 | 0%
54 | 150 | 2 | 4 | 0.25 | 31.6937 | 0.02235 | 85432.3011 | 5.5148 | 87.2458 | 88.236 | 307.854 | 554.1372 | 0% | 27.9285 | 500 | 1685.3076 | 6 | 0%
power vs. static head for 3" pipe, (4) optimum nozzle dia.
q (Usgpm) | static head (ft) | pipe dia (in) | no. of nozzles | nozzle dia. (in) | HF (ft) | f coef. | Reynolds no. | pipe velocity (ft/s) | nozzle velocity based on friction (ft/s) | single nozzle velocity (ft/s) | water jet power (1) nozzle (W) | power at turbine wheel (W) | % power increase compared to 1 nozzle | elec. cost per month | pipe length (ft) | turbine rpm | turbine dia. | turbine rpm increase %
79 | 25 | 3 | 4 | 0.5 | 8.519 | 0.021315 | 83322.8616 | 3.5857 | 32.5636 | 32.2715 | 60.2455 | 108.4419 | -3.703% | 5.4655 | 500 | 924.5785 | 4 | -1.25%
114 | 50 | 3 | 4 | 0.5 | 16.9809 | 0.020403 | 120238.0534 | 5.1743 | 46.0917 | 46.569 | 181.0331 | 325.8596 | 2.678% | 16.4233 | 500 | 1334.2018 | 4 | 0.885%
140 | 75 | 3 | 4 | 0.5 | 25.0736 | 0.019976 | 147660.7673 | 6.3544 | 56.6768 | 57.19 | 335.2954 | 603.5317 | 4.411% | 30.418 | 500 | 1092.329 | 6 | 1.449%
160 | 100 | 3 | 4 | 0.5 | 32.3414 | 0.019727 | 168755.1627 | 7.2622 | 65.9785 | 65.36 | 500.4993 | 900.8987 | -1.852% | 45.4053 | 500 | 1248.376 | 6 | -0.6211%
197 | 150 | 3 | 4 | 0.5 | 48.1689 | 0.019381 | 207779.794 | 8.9416 | 80.9433 | 80.4745 | 934.205 | 1681.569 | 0% | 84.7511 | 500 | 1537.063 | 6 | 0%
power vs. static head for 4" pipe, (4) optimum nozzle dia.
q (Usgpm) | static head (ft) | pipe dia (in) | no. of nozzles | nozzle dia. (in) | HF (ft) | f coef. | Reynolds no. | pipe velocity (ft/s) | nozzle velocity based on friction (ft/s) | single nozzle velocity (ft/s) | water jet power (1) nozzle (W) | power at turbine wheel (W) | % power increase compared to 1 nozzle | elec. cost per month | pipe length (ft) | turbine rpm | turbine dia. | turbine rpm increase %
175 | 25 | 4 | 4 | 0.75 | 9.0281 | 0.019398 | 138431.9694 | 4.468 | 32.0567 | 31.7722 | 129.3578 | 232.844 | 0% | 11.7353 | 500 | 910.2742 | 4 | 0%
250 | 50 | 4 | 4 | 0.75 | 17.7473 | 0.018685 | 197759.9562 | 6.3828 | 45.5537 | 45.3889 | 377.1364 | 678.8456 | 0% | 34.2138 | 500 | 1300.3917 | 4 | 0%
310 | 75 | 4 | 4 | 0.75 | 26.7651 | 0.018327 | 245222.3458 | 7.9147 | 55.7085 | 56.2822 | 719.0574 | 1294.3033 | 3.973% | 65.2329 | 500 | 1612.4857 | 4 | 1.307%
355 | 100 | 4 | 4 | 0.75 | 34.7149 | 0.018126 | 280819.1379 | 9.0636 | 64.8108 | 64.4522 | 1079.8502 | 1943.7304 | 0% | 97.964 | 500 | 1231.0374 | 6 | 0%
440 | 150 | 4 | 4 | 0.75 | 52.4989 | 0.017844 | 348057.523 | 11.2338 | 79.2037 | 79.8844 | 2056.0634 | 3700.9141 | 2.074% | 186.5261 | 500 | 1144.3447 | 8 | 0.6865%
power vs. static head for 6" pipe, (4) optimum nozzle dia.
q (Usgpm) | static head (ft) | pipe dia (in) | no. of nozzles | nozzle dia. (in) | HF (ft) | f coef. | Reynolds no. | pipe velocity (ft/s) | nozzle velocity based on friction (ft/s) | single nozzle velocity (ft/s) | water jet power (1) nozzle (W) | power at turbine wheel (W) | % power increase compared to 1 nozzle | elec. cost per month | pipe length (ft) | turbine rpm | turbine dia. | turbine rpm increase %
500 | 25 | 6 | 4 | 1.25 | 8.6423 | 0.017274 | 263679.9417 | 5.6736 | 32.4416 | 32.68 | 391.0151 | 703.8271 | 63% | 35.4729 | 500 | 936.282 | 4 | -16.28%
710 | 50 | 6 | 4 | 1.25 | 16.8817 | 0.016734 | 374425.5172 | 8.0565 | 46.161 | 46.4056 | 1119.5887 | 2015.2597 | 71.8% | 101.5691 | 500 | 1329.5204 | 4 | -14.8%
900 | 75 | 6 | 4 | 1.25 | 26.6379 | 0.016433 | 474623.895 | 10.2125 | 55.7819 | 58.824 | 2280.3998 | 4104.7197 | 86.52% | 206.8779 | 500 | 1123.5384 | 6 | -12.43%
1000 | 100 | 6 | 4 | 1.25 | 32.6483 | 0.016314 | 527359.8833 | 11.3472 | 65.8286 | 65.36 | 3128.1204 | 5630.6168 | 68.83% | 283.7831 | 500 | 1248.376 | 6 | -15.29%
1230 | 150 | 6 | 4 | 1.25 | 48.7593 | 0.016105 | 648652.6565 | 13.9571 | 80.7083 | 80.3928 | 5821.0161 | 10477.829 | 66.66% | 528.0826 | 500 | 1151.6269 | 8 | -15.66%
increase is due to limit on nozzle size of 1.5" on the single nozzle case.
Note: the calculations are a result of an iterative process, the flow number in column A must be changed up or down such that the velocity that corresponds to friction in column J is equal to the velocity that corresponds to flow in column K