## NPSHA Imp.
Pump system N.P.S.H.A calculation example (Imperial units) | [11 empty] | V1 (ft/s) | 0 | H1 (psi) | 0
J. Chaurette June 2016 | [8 empty] | acc. gravity | 32.17 |  | atmosph. press. (psia) | 14.7 | Vapor press. (psia) | 1
www.pumpfundamentals.com | [8 empty] | (ft/s^2) |  |  | elevation (ft)
Flow | Dia. | velocity | viscosity | Reynolds no. | pipe rough. | relative rough. | SG | frict. parameter | frict. factor | pipe length | pipe frict. loss | fittings loss | liquid surf. to ref. | suction cent. to ref. | vel. head 1 | press. head 1 | Equip. head loss | N.P.S.H.A.
(gpm) | (in) | (ft/s) | (cSt) |  | (ft) |  |  |  |  | (ft) | (ft) | (ft) | (ft) | (ft) | v1^2/2g | (ft) | (ft) | (ft)
(ft)
100 | 3 | 4.5389 | 1 | 105474.7 | 0.00015 | 0.0006 | 1 | 0.020706 | 2.652 | 15 | 0.3978 | 0 | 5 | 10 | 0 | 0 | 0 | 26.2492
Note: don't trust anyone, do your own calculations to verify these results,
verify the source of the formulas or develop them for yourself from basic principles,
secure yourself with a belt and suspenders, don't get caught with your pants down,
always sketch a flow schematic of your system including all the input data.
Yellow cells are inputs
The data used for the liquid are typical for water at 20 C
STEPS
1. determine flow rate
2. select pipe internal diameter
3. calculate velocity, determine if appropriate i.e between 3 and 6 ft/s, for new system adjust diameter
4. Calculate Reynolds number, determine if turbulent (i.e. above 4000)
5. input data: viscosity, specific gravity, pipe length, ilquid surface and suction centerline heights
inlet pressure head, inlet velocity, equipment head loss
6. input atmospheric pressure according to elevation (see tab below for chart)
7. input vapor pressure of liquid according to temperature (se tab below)
8. calculate the friction parameter with Swamee-Jain, check the value with the Moody diagram (see 5th tab)
9. calculate friction factor and pipe friction loss
10. calculate fittings (i.e. elbow, tees, reducers, etc.) using the Crane tech. paper 410 (neglected here)
to calculate use Cameron book data, Hydraulic Institute or other reliable source
or the Crane technical paper 410 |  |  |  | http://www.pumpfundamentals.com/help16.html
Formulas are located here:
http://www.pumpfundamentals.com/formula%20grab-bag.htm

## NPSHA metric
Pump system N.P.S.H.A calculation example (Imperial units) | [11 empty] | V1 (m/s) | 0 | H1 (kPa) | 0
J. Chaurette June 2016 | [8 empty] | acc. gravity | 9.81 |  | atmosph. press. (kPaa) | 101 | Vapor press. (kPaa) | 7
www.pumpfundamentals.com | [8 empty] | (m/s^2) |  |  | elevation (ft)
Flow | Dia. | velocity | viscosity | Reynolds no. | pipe rough. | relative rough. | SG | frict. parameter | frict. factor | pipe length | pipe frict. loss | fittings loss | liquid surf. to ref. | suction cent. to ref. | vel. head 1 | press. head 1 | Equip. head loss | N.P.S.H.A.
(l/min) | (mm) | (m/s) | (cSt) |  | (mm) |  |  |  |  | (m) | (m) | (m) | (m) | (m) | v1^2/2g | (m) | (m) | (m)
(m)
378.5 | 76.2 | 1.3833 | 1 | 105403.8058 | 0.045732 | 0.00060015 | 1 | 0.020708 | 2.6503 | 4.5732 | 0.1212 | 0 | 1.5244 | 3.0488 | 0 | 0 | 0 | 7.9424
Note: don't trust anyone, do your own calculations to verify these results,
verify the source of the formulas or develop them for yourself from basic principles,
secure yourself with a belt and suspenders, don't get caught with your pants down,
always sketch a flow schematic of your system including all the input data.
Yellow cells are inputs
The data used for the liquid are typical for water at 20 C
STEPS
1. determine flow rate
2. select pipe internal diameter
3. calculate velocity, determine if appropriate i.e between 3 and 6 ft/s, for new system adjust diameter
4. Calculate Reynolds number, determine if turbulent (i.e. above 4000)
5. input data: viscosity, specific gravity, pipe length, ilquid surface and suction centerline heights
inlet pressure head, inlet velocity, equipment head loss
6. calculate the friction parameter with Swamee-Jain, check the value with the Moody diagram (see 5th tab)
6. input atmospheric pressure according to elevation (see tab below for chart)
7. input vapor pressure of liquid according to temperature (se tab below)
7. calculate friction factor and pipe friction loss
8. calculate fittings (i.e. elbow, tees, reducers, etc.) using the Crane tech. paper 410 (neglected here)
to calculate use Cameron book data, Hydraulic Institute or other reliable source
or the Crane technical paper 410 |  |  |  | http://www.pumpfundamentals.com/help16.html
Formulas are located here:
http://www.pumpfundamentals.com/formula%20grab-bag.htm

## moody
Moody diagram based on the Colebrook equation